## Summary
TSHIAME WWTW REFURBISHMENT |  | C2.2
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026 |  | SUMMARY (Bidder)
SECTION | DESCRIPTION | AMOUNT R
SUMMARY OF PRINCIPAL SCHEDULES
A | SCHEDULE A1: PRELIMINARY AND GENERAL: ESTABLISHMENT
A | SCHEDULE A3 : P & G: MANAGEMENT, ENVIRONMENTAL, H & S COMPLIANCE
A | SCHEDULE A4 : P & G: TRAINING & COMMISSIONING
A | SCHEDULE A5 : P & G: MAINTENANCE & CONTRACTOR 1-YEAR O & M SUPPORT
SUB-TOTAL A: PRELIMINARIES & GENERAL
B | SCHEDULE B1 : DAYWORKS & PROVISIONAL
B | SCHEDULE B2 : TANK CLEANING, DEMOLITIONS & REPLACEMENT FENCING
B | SCHEDULE B3 : EARTHWORKS, PIPELINES AND ELECTRICAL CABLE DUCTS
B | SCHEDULE B4: BULK EARTHWORKS: SLUDGE DRYING BEDS & COMPOSTIING AREA
B | SCHEDULE B5: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
B | SCHEDULE B6: SLUDGE DRYING BEDS: CONCRETE WORKS (STRUCTURAL)
B | SCHEDULE B7: MODIFICATIONS & REPAIRS: CONCRETE WORKS (STRUCTURAL)
B | SCHEDULE B8: INTERAL ACCESS ROAD AND DRAINAGE
B | SCHEDULE B9: BIO-FILTER: RE-BUILD
B | SCHEDULE B10: BUILDING WORK: REFURB, RE-BUILD AND NEW (STRUCTURAL)
B | SCHEDULE B11: STEEL & METAL WORK (RAILINGS, VALVES, MISCELLANEOUS)
B | SCHEDULE B12: PONDS: SLUDGE REMOVAL & IMPROVEMENTS. EROSION PROTECTION
B | SCHEDULE B13: BUILDING WORKS - SPARES
SUB-TOTAL B: CIVIL WORKS
C | SCHEDULE C1 : ELECTRICAL: BULK FEEDER, TRANSFORMER & SWITCHGEAR
C | SCHEDULE C2 : ELECTRICAL: LV CABLES (RETIC)
C | SCHEDULE C3 : ELECTRICAL & ELECTRONIC: MCC's - INLET WORKS & MAIN PLANT ROOM
C | SCHEDULE C4 : ELECTRICAL & ELECTRONIC: CONTROL, PLC, TELEMETRY, INSTRUMENTS
C | SCHEDULE C5 : ELECTRICAL: BUILDINGS - ELECTRICAL INSTALLATIONS
C | SCHEDULE C6 : ELECTRICAL: SITE ILLUMINATION
C | SCHEDULE C7 : ELECTRICAL: STANDBY GENERATOR & ACCESSORIES
C | SCHEDULE C8 : ELECTRICAL: SECURITY SYSTEMS & REGS COMPLIANCE
C | SCHEDULE C9 : ELECTRICAL: EARTHING & LIGHTNING PROTECTION SYSTEM
C | SCHEDULE C10 : ELECTRICAL & ELECTRONIC: SPARES
SUB-TOTAL C: ELECTRICAL & ELECTRONIC WORKS
D | SCHEDULE D1 : MECHANICAL: INLET WORKS
D | SCHEDULE D2 : MECHANICAL: IMHOFF TANK WORKS
D | SCHEDULE D3 : MECHANICAL: BIOFILTER WORKS
D | SCHEDULE D4 : MECHANICAL: BIOREACTOR (BNRAS) WORKS
D | SCHEDULE D5 : MECHANICAL: CLARIFIER WORKS
D | SCHEDULE D6 : MECHANICAL: CHLORINATION WORKS
D | SCHEDULE D7 : MECHANICAL: MISCELLANEOUS WORKS
D | SCHEDULE D8 : MECHANICAL: SPARES
SUB-TOTAL D: MECHANICAL
T1 | SUB-TOTAL T1: A + B + C + D
ADD PROVISIONAL CONTINGENCIES OF 10% ON SUB-TOTAL T1 (see Vol 1A, Part C3 Scope of Work, payment item PSA7.1)
T2 | SUB-TOTAL T2
ADD PROVISIONAL CONTRACT PRICE ADJUSTMENT OF 10% ON SUB-TOTAL T2 (see Vol 1A, Part C3 Scope of Work, payment item PSA7.2)
T3 | SUB-TOTAL T2
ADD VAT (15%) ON SUB-TOTAL T2
T4 | TOTAL AMOUNT OF TENDER CARRIED FORWARD TO FORM OF OFFER

## Sche A1
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
SCHEDULE A1: PRELIMINARY AND GENERAL
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
A1 | SANS 1200A, PSA | SCHEDULE A1: PRELIMINARY AND GENERAL
A1.1 | PSAB | SCHEDULE 1.1 : FIXED-CHARGE ITEMS
A1.1.1 | SANS 1200A 8.3.1 | Contractual requirements | Sum | 1
Establishment of facilities on site
A1.1.2 | SANS 1200 A 8.3.2 | .1 Facilities for the Engineer/Employer
A1.1.2.1 | PSAB1 | (a) Nameboard | no | 1
A1.1.2.2 | SANS 1200 A 8.3.2.1 a), PSAB2.1 | (b) Furnished office x 1 no (with 2 desks & 2 chairs) | Sum | 1
A1.1.2.3 | SANS 1200 A, 7.2 & 8.3.2.2, PSAB2.2 | (c) Testing (laboratory equipment) | Sum | 1
A1.1.2.3 | PSAB3 | (d) Survey equipment | Sum | 1
A1.1.3 | SANS 1200 A 4.2 & 8.3.2.2, PSA2 | .2 Facilities for the Contractor (inclusive for all sub-contractors)
A1.1.3.1 | PSA2.1 | (a) Offices and storage sheds | Sum | 1
A1.1.3.2 |  | (b) Workshops (at Contractor discretion) | Sum | 1
A1.1.3.4 | PSA2.6 | (d) Living accommodation (off-site allowance) | Sum | 1
A1.1.3.5 | PSA2.5 | (e) Ablution and latrine facilities | Sum | 1
A1.1.3.6 | SANS 1200 A 8.3.2.2, 8.3.2.3 | (f) Tools and equipment | Sum | 1
A1.1.3.7 | PSA2.2, PSA2.3 | (g) Water supplies, power and communications | Sum | 1
A1.1.3.8 | SANS 1200 A, 5.5 | (h) Dealing with water (Sub-clause 5.5) | Sum | 1
A1.1.3.9 | SANS 1200 A, 5.8 | (i) Access (Sub-clause 5.8) | Sum | 1
A1.1.3.10 | SANS 1200 A 8.3.2.2, 8.3.2.3 | (j) Plant (designated plant only, incl. sieving equipment / plant for sieving and sorting of existing bio-filter stone media) | Sum | 1
A1.1.4 | SANS 1200 A, 8.3.3 | Other fixed-charge obligations | Sum | 1
A1.1.5 | SANS 1200 A, 8.3.4 | Removal of Contractor's and Engineer's site establishment on completion | Sum | 1
Total Carried Forward
C2.2-1-1
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
SCHEDULE 1: PRELIMINARY AND GENERAL
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
A1.2 |  | SCHEDULE 1.2 : TIME-RELATED ITEMS
A1.2.1 a) | 8.4.1 | Contractual requirements | Sum | 1
A1.2.2 | 8.4.2 | .1 Facilities for the Engineer/Employer
| PSAB1 | (a) Nameboard | no | 1
| PSAB2.1 | (b) Furnished office (with 2 desks & 2 chairs) | Sum | 1
| PSAB2.2 | (c) Testing (Laboratory equipment) | Sum | 1
| PSAB3 | (d) Survey equipment | Sum | 1
A1.2.3 | 8.4.2 | .2 Facilities for the Contractor
|  | (a) Offices and storage sheds | Sum | 1
|  | (b) Workshops (at Contractor discretion) | Sum | 1
|  | (d) Living accommodation (off-site allowance) | Sum | 1
|  | (e) Ablution and latrine facilities | Sum | 1
|  | (f) Tools and equipment | Sum | 1
|  | (g) Water supplies, power and communications | Sum | 1
|  | (h) Dealing with water (Sub-clause 5.5) | Sum | 1
|  | (i) Access (Sub-clause 5.8) | Sum | 1
|  | (j) Plant | Sum | 1
A1.2.4 | 8.4.3 | Supervision for duration of construction | Sum | 1
PRELIMINARY AND GENERAL CHARGES (MAIN CONTRACTOR - SUBCONTRACTOR)
A1.2.5 | 8.4.3 | Main Contractor's mark-up for attendance and management of sub-contractors (including cost of Construction Manager) | Sum | 1
PRELIMINARY AND GENERAL CHARGES (LOCAL SUBCONTRACTORS/CPG CONTRACTORS)
A1.2.6 | 8.4.3 | Main Contractor's mark-up for attendance and management of local sub-contractors (including cost of Construction Manager) | Sum | 1
The Main Contractor cost shall include for the administrative and technical management of the sub-contractor and all related charges, costs and profit for the above items
A1.2.7 | 8.4.4 | Company and head office overhead costs for the duration of the Contract | Sum | 1
A1.2.8 | 8.4.5 | Other time-related obligations | Sum | 1
Total Carried Forward To Summary

## Sche A3
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE A3 : MANAGEMENT, ENVIRONMENTAL, HEALTH & SAFETY COMPLIANCE | SCHEDULE A3 : MANAGEMENT, ENVIRONMENTAL, HEALTH & SAFETY COMPLIANCE | SCHEDULE A3 : MANAGEMENT, ENVIRONMENTAL, HEALTH & SAFETY COMPLIANCE | SCHEDULE A3 : MANAGEMENT, ENVIRONMENTAL, HEALTH & SAFETY COMPLIANCE
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
A3 |  | SCHEDULE A3 : MANAGEMENT, ENVIRONMENTAL, HEALTH & SAFETY COMPLIANCE
A3.1 | PSA5 | Other General Fixed-charge Items
A3.1.1 | PSA5.1 | LEP Plan
A3.1.1.1 | PSA5.1, 8.3.5.1 | Provision of a suitable Local Economic Participation Plan (rate includes auditing by a recognised external auditing firm of the Contractor's expenditure on local goods, services and labour as defined in the mentioned specifications. Two audits shall be included) | Sum | 1
A3.1.2 | PSA5.3 | Contractor's obligations in respect of Health and Safety
A3.1.2.1 | PSA5.3, 8.3.5.3 | (a) Health and Safety Plan - Prepare & Maintain for all works (including Civils, Mechanical, Electrical & Electronic Works) | Sum | 1
A3.1.2.2 | PSA5.3, 8.3.5.3 | (b) Compliance with the Occupational Health and Safety Act (Act 85 of 1993) and its regulations and with the Employers Health and Safety Specification | Sum | 1
A3.1.3 | PSA 5.4 | Contractor's obligations in respect of Environmental Management:
| PSA 5.4, 8.3.5.4 | Compliance with the Client's Environmental Management programme and all South African Environmental Legislation & Regulations (Fixed Charge Item)
A3.1.3.1 | PSA 5.4 (a), 8.3.5.4 | i) Prepare & maintain key documents, incl. but not limited to: Waste Management Plan, Emergency Contingency Plans (Environmental Incident), Fire Prevention & Management Plan, Create and maintain an Environmental File with all relevant information and plans as indicated in the Client's Environmental Management Programme (Plan) specification no S-EMP. | Sum | 1
A3.1.3.2 | PSA 5.4 (a), 8.3.5.4 | ii)Compliance with Environmental Management and Client EMPr Specification Requirements: Construction Phase (inclusive of testing, training and commissioning of refurbished works): Contractor Works - all other fixed charge cost items not mentioned under A3.1.3.1 and excludes cost of DEO (measured elsewhere, see A3.2) | Sum | 1
Total Carried Forward
C2.2-1-1
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
SCHEDULE A3 : MANAGEMENT, ENVIRONMENTAL, HEALTH & SAFETY COMPLIANCE
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
A3.1.4 | PSA7.12 | Specialist Studies (as and when instructed by the Employer's Agent), using a 3-quotation process Fixed Charge items
A3.1.4.1 | PSA7.12 | Professional Registered Aquatic Scientist (to establish a bio-monitoring programme) as per Water Use Licence Condition 3.1.4. Undertake water habitat / species survey & produce report with bio-monitoring programme | Prov Sum | 1 | 60000 | 60000
A3.1.4.2 | PSA7.12 | Professional Registered Geohydrologist (to prepare Geohydrological Report) as per Water Use Licence Condition 15.3. Includes management time to oversee drilling and protection of 3 no of monitoring boreholes. Prepare geohydological report and hydrocensus to evaluate potential for ground water being impacted upon | Prov Sum | 1 | 70000 | 70000
A3.1.4.3 | PSA7.12 | Specialist Drilling Contractor: To drill 3 no of monitoring borehole up to 120mm in internal diameter and up to 50m deep. Collect water quality sampling and step-test pumping as directed by Geohydrological Engineer. Install dipping tube for future monitoring purposes and provide capped headplate with opening for 32mm dia dipping tube. Place headworks inside secure concrete manhole, 1.2m internal diameter | Prov Sum | 1 | 210000 | 210000
A3.1.4.4 |  | Other Specialist (on a needs basis only) | Prov Sum | 1 | 30000 | 30000
A3.1.4.5 | PSA7.12 | Environmental Compliance (continues): Laboratory testing & analysis: waste sludge | Prov Sum | 1 | 20000 | 20000
A3.1.4.6 | PSA7.12 | Environmental Compliance (continues): Laboratory water quality testing & analysis: River water (upstream & downstream as per Water Use Licence & amendment) | Prov Sum | 1 | 20000 | 20000
A3.1.4.7 | PSA7.12 | Overhead, Charges and Profit (on items A3.1.4.1 to A3.1.4.6) | % |  | 410000
A3.1.5 |  | DOCUMENTATION: AS-BUILT DRAWINGS
As-built drawings shall be prepared in hard-copy and electronic format as specified in the Scope of Work Document
A3.1.5.1 | PSA5.5, 8.3.5.5 | Provision of as-built drawings & details: Civils | Sum | 1
A3.1.5.2 | PSA5.5, 8.3.5.5 | Provision of as-built drawings & details: Structures | Sum | 1
A3.1.5.3 | PSA5.5, 8.3.5.5 | Provision of as-built drawings & details: Mechanical & Process | Sum | 1
A3.1.5.4 | PSA5.5, 8.3.5.5 | Provision of as-built drawings & details: Electrical | Sum | 1
A3.1.5.5 | PSA5.5, 8.3.5.5 | Provision of as-built drawings & details: Electronic | Sum | 1
Total Carried Forward
C2.2-1-1
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
SCHEDULE A3 : MANAGEMENT, ENVIRONMENTAL, HEALTH & SAFETY COMPLIANCE
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
A3.1.6 |  | DOCUMENTATION: OPERATION & MAINTENANCE (0 & M Manuals)
A3.1.6.1 | PSA5.6 | Prepare Operations & Maintenance Manuals in the required format (hard-copies and electronic copies as specified in the Scope of Work document and notably the Particular Management Specification document SB (O & M Manual Specification) | Sum | 1
NOTE | NOTE ONLY | Operation & Maintenance test equipment & consumables are measured seperately as indicated in Schedule D7 (Mechanical: Miscellaneous Works) | n/a | n/a | n/a
A3.2 | SANS 1200 A, 8.4.5, PSA6 | Other General Time-Related Charge Items
A3.2.1 | 8.3.6.1, PSA6.1 | Occupational Health and Safety compliance with Occupational Health and Safety Act (Act 85 of 1993) and its regulations and with the Employers Health and Safety Specification, for the following periods:
A3.2.1.1 | 8.3.6.1 (a), PSA6.1 | (a) Compliance with Health and Safety Requirements: Construction Phase (inclusive of testing, training and commissioning of refurbished works): Contractor Works | Sum | 1
A3.2.1.2 | 8.3.6.1 (b), PSA6.1, PSA7.12 | (b)(i) Compliance with Health and Safety Requirements: Construction Phase (inclusive of testing, training and commissioning of refurbished works): Employer’s appointed Health and Safety Agent | Prov Sum | 1 | 144000 | 144000
A3.2.1.3 | 8.3.6.1 (b), PSA6.1 | (ii) Overheads, charges & profit on item A3.2.1.2, (b)(i) | % | 8 | 144000
A3.2.1.4 | 8.3.6.1 (c), PSA6.1 | Compliance with Health and Safety Requirements: Post-Commissioning, Contractor 1-year Operations & Maintenance (O & M) Support period | Sum | 1
A3.2.2 | 8.3.6.2, PSA6.2 | Environmental Management Compliance
A3.2.2.1 | 8.3.6.2 (a), PSA6.2 | (a) Compliance with Environmental Management Requirements (with appointed DEO): Construction Phase (inclusive of testing, training and commissioning of refurbished works but excludes Contractor 1-year O & M Support period that is overseen by MaP Water): Contractor Works, inclusive of Contractor appointed DEO (Designated Environmental Officer) for duration of contruction and commissioning period as described in the contract documents | Sum | 1
A3.2.2.2 | 8.3.6.2 (b), PSA6.2 & PSA7.12 | (b) Compliance with Environmental Management Requirements (with appointed ECO): Construction Phase (inclusive of testing, training and commissioning of refurbished works): Employer’s appointed (independent) ECO (Environmental Control Officer). Part-time monitoring for duration of construction but excl. 1-year Contractor 0 & M support period. | Prov Sum | 1 | 160000 | 160000
A3.2.2.3 | 8.3.6.2 (b), PSA6.2 & PSA7.12 | (ii) Overheads, charges & profit on item A3.2.2.2 | % |  | 160000
Total Carried Forward
C2.2-1-1
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
SCHEDULE A3 : MANAGEMENT, ENVIRONMENTAL, HEALTH & SAFETY COMPLIANCE
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
A3.2.3 | PSA6.3 | c) Security
A3.2.3.1 | PSA6.3, 8.3.6.3 | Provision of adequate security (construction & commissioning phase but excluding 1-year Contractor ) & M support period) | Sum | 1
A3.3 |  | Other Sums Stated Provisionally by the Engineer
A3.3.1 | 8.5 | (a) .1 Community requirements
A3.3.1.1 | PSA7.3 | .1 CLO remuneration | Prov sum | 1 | 224870.4 | 224870.4
A3.3.1.2 |  | .2 Overheads, charges and profit on above | % |  | 224870.4
A3.3.2 | 8.5 | (b) .2 Engineer's requirements
A3.3.2.1 | PSA7.5 | .1 Engineer's cellular phone costs | Prov sum | 14400 | 1 | 14400
A3.3.2.2 |  | .2 Overheads, charges and profit on above | % |  | 14400
A3.3.2.3 | PSA7.6 | .3 Engineer's site office consumables (stationary) | Prov sum | 4800 | 1 | 4800
A3.3.2.4 |  | .4 Overheads, charges and profit on above | % |  | 4800
A3.3.2.5 | PSA7.7 | .5 Electronic equipment | Prov sum | 45000 | 1 | 45000
A3.3.2.6 |  | .6 Overheads, charges and profit on above | % |  | 45000
Total Carried Forward To Summary

## Sche A4
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE A4 : TRAINING & COMMISSIONING | SCHEDULE A4 : TRAINING & COMMISSIONING | SCHEDULE A4 : TRAINING & COMMISSIONING | SCHEDULE A4 : TRAINING & COMMISSIONING
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
A4 |  | SCHEDULE A4 : TRAINING & COMMISSIONING
A4.1 |  | OTHER GENERAL CHARGES: TRAINING
A4.1.1 | PSA5.8 & SD6.1 | Development of a Syllabus for Process Controllers and Maintenance Personnel
A4.1.1.1 | PSA5.8 & SD6.1.1 | Develop syllabus and training material for SAQA accredited training for process controllers (30 credits). Refer to Additional Management Specification "SD" | PC Sum | 1 | 30000 | 30000
A4.1.1.2 | PSA5.8 & SD6.1.2 | Develop training material for maintenance personnel | PC Sum | 1 | 50000 | 50000
A4.1.1.3 | PSA5.8 | Attendance and Profit | % |  | 50000
A4.1.2 | PSA5.8 & SD6.2 | Conduct knowledge transfer and skills development for process controllers
A4.1.2.1 | PSA5.8 & SD6.2 | For a group of 6 learners (process controllers and learner process controllers) : conduct skills program consisting of 30 credits | PC Sum | 1 | 250000 | 250000
A4.1.2.2 | PSA5.8 & SD6.2 | Attendance and Profit | % |  | 250000
A4.1.3 | PSA5.8 & SD6.3 | Conduct Knowledge Transfer and Skills Development for Maintenance Personnel
A4.1.3.1 | PSA5.8 & SD6.3 | Conduct a 5-day training course, including lectures, demonstrations, on site training and practical’s for maintenance staff | PC Sum | 1 | 80000 | 80000
A4.1.3.2 | PSA5.8 & SD6.3 | Attendance and Profit | % |  | 80000
A4.1.4 |  | Conduct Training and Skills Development for Process Controllers and Maintenance Personnel in Operation and Maintenance of the PLC System
A4.1.4.1 | PE-PLC-26.3 | Conduct a 2-day training course, including lectures, demonstrations, on site training and practical’s for Process Controllers and Maintenance Personnel (excludes General Workers). Allowance for total number of people to be trained: 8 no | PC Sum | 1 | 30000 | 30000
A4.1.4.1 | PE-PLC-26.3 | Attendance and Profit on item A4.1.4.1 | % |  | 30000
Total Carried Forward
C2.2-1-1
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
SCHEDULE A4 : TRAINING & COMMISSIONING
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
A4.3 |  | TESTING AND COMMISSIONING OF THE WASTEWATER TREATMENT WORKS
A4.3.1 | PSA5.7 & SC 12.1 | Decommmissioning and removal of installations as part of the system
A4.3.1.1 | PSA5.7 & SC 12.1 | Existing inlet works, Imhoff tanks and associated pipework and structures (EXCLUDING. drain-down and removal of wastewater and silt / sludge & cleaning as measured under Civils) | Sum | 1
A4.3.1.2 | PSA5.7 & SC 12.1 | Biofilter distribution arm, associated pipework and steel structures, but EXCLUDING dismantling the biofilter rock media for grading and reconstruction (see Civils Schedule B8) | Sum | 1
A4.3.1.3 | PSA5.7 & SC 12.1 | Existing BNRAS reactor, clarifier, with associated pipework and structures (but EXCLUDING. drain-down and removal of wastewater and silt / sludge & cleaning as measured under Civils) | Sum | 1
A4.3.1.4 | PSA5.7 & SC 12.1 | Existing ponds and effluent pipework and structures, but EXCLUDING removal and handling of sludge (as measured seperately under Civils, Schedule B11) | Sum | 1
A4.3.2 | NOTE ONLY | Dry Testing: Of mechanical-electrical and electrical / electronic equipment is included in Schedule C and D respectively | n/a | n/a | n/a | n/a
A4.3.2.1 | PEI-PLC-26.3 | Dry testing (pre-commissioning) & Commissioning of the whole electronic installation system for this WWTW. This notably includes amongst other the two PLC units (1 unit at the Inlet Works MCC panel and 1 unit at the Main MCC Plant Room). Wet testing is priced further below | Sum | 1
A4.3.3 | SC 12.2 | Testing and Commissioning of an Installation
A4.3.3.1 | PSA5.7.1 & SC 12.2 | Clean Wet Commissioning of installations as defined and specified in SC 11.2.1: | - | - | -
A4.3.3.1.1 | PSA5.7.1 & SC 12.2 | Installation 2: Inlet works and Imhoff tanks | Sum | 1
A4.3.3.1.2 | PSA5.7.1 & SC 12.2 | Installation 3: Biological Trickling Filter | Sum | 1
A4.3.2.1.3 | PSA5.7.1 & SC 12.2 | Installation 4: Biological Nutrient Removal Activated Sludge Process | Sum | 1
A4.3.3.1.4 | PSA5.7.1 & SC 12.2 | Installation 5: Sludge drying beds, associated valves and pipework | Sum | 1
A4.3.3.1.5 | PSA5.7.1 & SC 12.2 | Installation 6: Maturation (Effluent Ponds) and associated equipment (fill ponds with treated effluent from Clarifier process unit with chlorination added) | Sum | 1
A4.3.4 |  | Testing and Commissioning of the Installations as a whole
A4.3.4.1 | PSA5.7.2 & SC 12.3.1 | Final Wet Commissioning of the treatment system, including Installations 2, 3, 4, 5 and 6 as defined and specified in SC 11.2.2, commencing with the Day_01 tests and concluding with the successful completion of the Day_60 tests. | Sum | 1
A4.3.4.2 | PSA5.7.2 & SC 12.3.2 | Extra over A4.3.3.1 above, for the Professional Process Controller supervision (PrPC Water) for the duration of full wet commissioning and process tests with raw wastewater | PC Sum | 1 | 214580 | 214580
A4.3.4.3 | PSA5.7.2 & SC 12.3.3 | Attendance and Profit for Professional Process Controller supervision (item A4.3.3.2) | % |  | 214580
A4.3.4.4 | PSA5.7.2 & SC 12.3.4 | Calibration of equipment set-points by Contractor's Electro-Mechanical commissioning team, based on PrPC Water instructions | Sum | 1
Chemicals
A4.3.5 | PSA5.10 | Supply of chemicals during trial operation period | Prov Sum | 1 | 60000 | 60000
Total Carried Forward To Summary

## Sche A5
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE A5 : MAINTENANCE & CONTRACTOR 1-YEAR O & M SUPPORT PERIOD | SCHEDULE A4 : TRAINING & COMMISSIONING | SCHEDULE A4 : TRAINING & COMMISSIONING | SCHEDULE A4 : TRAINING & COMMISSIONING
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
A5 |  | SCHEDULE A5 : MAINTENANCE & CONTRACTOR 1-YEAR O & M SUPPORT PERIOD
A5.1 |  | OTHER GENERAL CHARGES: MAINTENANCE DURING THE REFURBISHMENT WORK, PRIOR TO PRACTICAL COMPLETION
A5.1.1 | PSA7.13 & SA 6.2 | Maintenance of an Installation prior to Practical Completion of Installation 1 (General Site Work): General Works (see Additional Management Specification SA, clause SA 2.4.1 for detail description of installation) | sum | 1
A5.1.2 | PSA7.13 & SA 6.2 | Maintenance of an Installation prior to Practical Completion of Installation 2 (Inlet Works): General Works (see Additional Management Specification SA, clause SA 2.4.1 for detail description of installation) | sum | 1
A5.1.3 | PSA7.13 & SA 6.2 | Maintenance of an Installation prior to Practical Completion of Installation 3: General Works (see Additional Management Specification SA, clause SA 2.4.1 for detail description of installation) | sum | 1
A5.1.4 | PSA7.13 & SA 6.2 | Maintenance of an Installation prior to Practical Completion of Installation 4: General Works (see Additional Management Specification SA, clause SA 2.4.1 for detail description of installation) | sum | 1
A5.1.5 | PSA7.13 & SA 6.2 | Maintenance of an Installation prior to Practical Completion of Installation 5: General Works (see Additional Management Specification SA, clause SA 2.4.1 for detail description of installation) | sum | 1
A5.1.6 | PSA7.13 & SA 6.2 | Maintenance of an Installation prior to Practical Completion of Installation 6 (Effluent Ponds / Sludge Lagoons): General Works (see Additional Management Specification SA, clause SA 2.4.1 for detail description of installation) | sum | 1
A5.1.7.1 | 8.5 b) & SA 6.3.2 | Materials and/or equipment to be supplied and /or third party work to be executed by the Employer or Employer's Representative (Engineer) or Municipality's WSP (MaP Water) in support of Operation and Maintenance works when approved by the Employer | Prov sum | 1 | 100000 | 100000
A5.1.7.2 |  | Overheads, charges and profit on above | % | 100000
A5.2 |  | OTHER GENERAL CHARGES: O & M SUPPORT PERIOD (AFTER FINAL WET COMMISSIONING & COINCIDING WITH 1-YEAR DEFECTS LIABILITY PERIOD)
A5.2.1 | PSA7.14 | 1-year post comissioning Operation and Maintenance assistance
A5.2.1.1 | 8.5 b) | Management Staff (1 no x 20% of time/ month), Class V Process Controller Water (1 no x 100% of time / mnth) , Class III Pr. PC Water (1 no x 100% of time / mnth). Mechanical & Electrical Maintenance staff / Artisans (2 no 25% of time/month each) and 2 x General Workers (2 no x 100% of time/month each) each. | Months | 12
A5.2.1.2 |  | Accommodation for Contractor staff within 20km of site | Months | 12
A5.2.1.3 |  | Travel (all inclusive, incl. fuel, maint, services), with Contractor providing own support (at least on vehicle / SUV / light delivery vehicle) | Months | 12
Total Carried Forward
C2.2-1-1
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
SCHEDULE A5 : MAINTENANCE & CONTRACTOR 1-YEAR O & M SUPPORT PERIOD
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
A5.2.2 |  | Water Quality Monitoring, Sampling & Analysis
A5.2.2.1 | PSA7.15 | Water quality sampling, monitoring and analysis (analysis by SANAS accredited laboratory) | Prov sum | 168000 | 1 | 168000
A5.2.2.2 |  | .Overheads, charges and profit on above | % | 168000
A5.2.3 |  | Alarm monitoring Service
A5.2.3.1 |  | Monthly monitoring charge | Prov sum | 120000 | 1 | 120000
A5.2.3.2 |  | Overheads, charges and profit on above | % | 120000
A5.2.4 |  | Transformer & Diesel Generator: annual inspection by external Service Provider as approved by the Employer's Representative
A5.2.4.1 |  | Mains Power 400 kVA Transformer: Annual Service fee for 1 year | Prov sum | 54000 | 1 | 54000
A5.2.4.2 |  | Diesel Generator: Annual inspection and maintenance of 300 kVA unit by Supplier and/or Supplier Approved Contractor. Excludes ordinary monthly maintenance as be done by Principal Contractor | Prov sum | 54000 | 1 | 54000
A5.2.4.3 |  | Overheads, charges and profit on above items A5.2.4.1 and A5.2.4.2 | % | 108000
A5.2.5 |  | Maintenance equipment and Laboratory Equipment
A5.2.5.1 | PSA7.17 | Maintenance equipment and Laboratory Equipment (to be agreed with the Employer's Representative). This exclude light delivery vehicles & spares (see item A5.5.1) | Prov sum | 1 | 50000 | 50000
A5.2.5.1 |  | Overheads, charges and profit on above | % | 50000
A5.2.6 |  | Chemicals (12-months, post commissioning)
A5.2.6.1 |  | Chlorination (65% solution) | Prov sum | 1 | 178560 | 178560
A5.2.6.2 |  | Chloride of lime, kg | Prov sum | 1 | 1560 | 1560
A5.2.6.3 |  | On-site Chemicals, Process Control | Prov sum | 1 | 30000 | 30000
A5.2.6.4 |  | Overheads, charges and profit on above items: A5.2.6.1, A5.2.6.2 and A5.2.6.3 | % | 210120
A5.2.6.5 |  | H&S Cleansing chemicals (consumables) | Sum | 1
A5.2.7 |  | Diesel & Lubricant Allowance - For Maintenance Only (excludes running of stand-by power unit during mains power load shedding / emergency / Eskom / Municipal imposed power cuts)
A5.2.7.1 |  | Diesel & Lubricant Allowance - For Maintenance Only | Prov sum | 1 | 96000 | 96000
A5.2.7.1 |  | Overheads, charges and profit on above items A5.2.7.1 | % | 96000
Total Carried Forward
C2.2-1-1
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
SCHEDULE A5 : MAINTENANCE & CONTRACTOR 1-YEAR O & M SUPPORT PERIOD
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
A5.5 |  | OTHER GENERAL CHARGES THAT IS EXCLUDED FROM CONTRACTOR O & M SUPPORT PERIOD PRICING
A5.5.1 |  | Spares for Equipment
A5.5.1.1 |  | Spares for Structures / Building Works as agreed with the Employer's Representative (refer to Civils, Schedule B13 for price allowance for Year 1 of Operations) | n/a |  |  | n/a
A5.5.1.2 |  | Spares for Mechanical Works as agreed with the Employer's Representative (refer to Mechanical, Schedule D8 for price allowance for Year 1 of Operations) | n/a |  |  | n/a
A5.5.1.3 |  | Spares for Electrical & Electronic Works as agreed with the Employer's Representative (refer to Electrical, Schedule C10 for price allowance for Year 1 of Operations) | n/a |  |  | n/a
A5.5.2 |  | Electrical Cost & Charges
A5.5.2.1 |  | Paid for by the Municipality | n/a |  |  | n/a
A5.5.3 |  | Municipal Staff as allocated to Tshiame WWTW
A5.5.3.1 |  | Paid for by the Municipality | n/a |  |  | n/a
A5.5.4 |  | Security Staff (Municipal and /or Private), 24-hr
A5.5.4.1 |  | Paid for by the Municipality | n/a |  |  | n/a
A5.5.5 |  | Standby-Power Diesel for Diesel Generator
A5.5.5.1 |  | Paid for by the Municipality | n/a |  |  | n/a
Total Carried Forward To Summary

## Sche B1_n
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
SCHEDULE B1 : DAYWORKS & PROVISIONAL
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B1 | SANS 1200A | SCHEDULE B1 : DAYWORKS & PROVISIONAL SUMS
B1.1 |  | DAYWORKS AND TEMPORARY WORKS
| 8.7 | DAYWORKS
Note:Dayworks to be executed on instruction of the Engineer/Employer only
LABOUR BY CLASS
B1.1.1 | 8.7.1 | (a) Skilled | hr | 8 | 35
|  | (b) Semi-skilled | hr | 8 | 30
|  | (c) Unskilled | hr | 8 | 28
LABOUR BY TRADE
|  | Construction Hand (General Worker) | hr | 8 | 45
|  | Plant Operator | hr | 8 | 55
|  | Carpenter | hr | 8 | 80
|  | Clerk | hr | 8 | 60
|  | Steel Fixer | hr | 8 | 80
|  | Bricklayer or Plasterer | hr | 8 | 60
|  | Welder or Steel Worker | hr | 8 | 90
|  | Artisan - Mechanical | hr | 8 | 75
|  | Artisan - Electrical and /or Electronic | hr | 8 | 75
|  | Gang Leader or Section Leader or Junior Foreman | hr | 8 | 80
|  | Senior Foreman | hr | 8 | 150
|  | Site Engineer (Junior) | hr | 8 | 250
|  | Site Engineer (Senior) | hr | 8 | 850
|  | Site Agent | hr | 8 | 950
|  | Contract Manager | hr | 8 | 1200
|  | Environmental Officer (Junior) | hr | 8 | 350
|  | Environmental Officer (Senior) | hr | 8 | 950
|  | Health & Safety Officer (Junior) | hr | 8 | 250
|  | Health & Safety Officer (Senior) | hr | 8 | 950
|  | Security Guard (qualified and unarmed) | hr | 8 | 80
|  | Security Guard (qualified & armed with firearm) | hr | 8 | 130
Total Carried Forward
#REF!
SCHEDULE OF QUANTITIES
SCHEDULE 2 : DAYWORKS & PROVISIONAL SUMS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
OTHER PROFESSIONAL LABOUR BY TRADE
Labour for As-built Survey following cleaning and drain-down of tanks as described in the Scope of Work:
|  | Professional Land Surveyor Inclusive of all equipment, 2 no of assistants and electronic processing of data to generate AutoCAD drawing file and Excel based spreadsheet with Z, Y and Z coordinates & confirmation of requested dimensions | day | 5 | 10000
OTHER PROFESSIONAL LABOUR BY TRADE
Miscellaneous
|  | Professional Registered Electronic Engineer (Pr Eng / Pr Tech Eng) | hr | 8 | 1000
|  | Professional Registered Electric Engineer (Pr Eng / Pr Tech Eng) | hr | 8 | 1000
|  | Professional Registered Mechanical Engineer (Pr Eng / Pr Tech Eng) | hr | 8 | 1000
|  | Professional Registered Process Engineer (Pr Eng / Pr Tech Eng) | hr | 8 | 1400
|  | Professional Registered Civil Engineer (Pr Eng / Pr Tech Eng) | hr | 8 | 1000
WWTW - OPERATIONS & MAINTENANCE STAFF
|  | M & E Maint - Qualified Artisan | hr | 8 | 285
|  | Management - Manager | hr | 8 | 485
|  | Class V - Process Controller (PrPc) | hr | 8 | 313
|  | Class IV - Process Controller (PrPc) | hr | 8 | 255
|  | Class III - Process Controller (PrPc) | hr | 8 | 171
|  | Class II - Process Controller (PrPc) | hr | 8 | 143
|  | Class I - Process Controller (PrPc) | hr | 8 | 85
|  | Class 0 - Process Controller (PrPc) | hr | 8 | 57
|  | Day worker or General Worker | hr | 8 | 45
Total Carried Forward
#REF!
SCHEDULE OF QUANTITIES
SCHEDULE 2 : DAYWORKS & PROVISIONAL SUMS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
PLANTHIRE (WORK RATES ON SITE)
All rates are wet rates and inclusive of Operator unless otherwise indicated
B1.1.2 |  | TRUCKS
| 8.7.2 | .1 Tipper trucks (specify capacity)
|  | (a) Capacity__6___m³ (small) | hr | 8 | 900
|  | (b) Capacity__10___m³ (medium) | hr | 8 | 1000
|  | (c) Capacity_ 40____m³ (large) | hr | 8 | 2000
| 8.7.2 | .2 Flatbed trucks (specify capacity)
|  | (a) Capacity_____m³ (small) | hr | 8 | 900
|  | (b) Capacity_____m³ (medium) | hr | 8 | 1000
|  | (c) Capacity_____m³ (large) | hr | 8 | 1200
LDV'S
B1.1.3 | 8.7.2 | .3 LDV (specify size)
|  | (a) LDV__1___ton | km | 200 | 6.5
|  | (a) LDV__3___ton | km | 200 | 7
WATER TANKERS
B1.1.4 | 8.7.2 | .4 Water tankers (specify capacity)
|  | (a) Capacity___5000___liter (small, towable) | hr | 8 | 800
|  | (b) Capacity__10,000____liter (medium) | hr | 8 | 1000
B1.1.5 |  | BULLDOZER
B1.1.5.1 |  | Bulldozer & Ripper (D6 or equivalent) | hr | 8 | 1000
B1.1.6 |  | FRONT END WHEEL LOADERS
B1.1.6.1 | 8.7.2 | Front end wheel loader (Cat 950 or similar) | hr | 8 | 500
B1.1.7 |  | GRADERS
B1.1.7.1 | 8.7.2 | Grader (120G or equivalent) | hr | 8 | 500
EXCAVATORS
B1.1.7 | 8.7.2 | .7 Crawler excavators (specify model/mass/kW)
|  | (a) Model____/_____/kg____kW (small) | hr | 8 | 1000
|  | (b) Model____/_____/kg____kW (medium) | hr | 8 | 1200
|  | (c) Model____/_____/kg____kW (large) | hr | 8 | 1300
|  | Back acting excavators (Hitachi EX200 or similar) | hr | 8 | 990
Total Carried Forward
C2.2-2-2
#REF!
SCHEDULE OF QUANTITIES
SCHEDULE 2 : DAYWORKS & PROVISIONAL SUMS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
TLB'S
B1.1.8 | 8.7.2 | .8 Tractor loader backhoe (TLB)(specify model)
|  | (a) Model__________ | hr | 8 | 900
B1.1.9 |  | ROLLERS
| 8.7.2 | .9 Self propelled vibrating rollers (smooth drum) (specify mass)
|  | (a) Mass_____kg (medium) | hr | 0
|  | (b) Mass_____kg (large) | hr | 0
| 8.7.2 | .10 Self propelled vibrating rollers (padfoot) (specify mass)
|  | (a) Mass_____kg (medium) | hr | 0
|  | (b) Mass_____kg (large) | hr | 0
|  | Roller / Compactor (D72Y or equivalent) | hr | 8 | 1000
B1.1.10 |  | COMPACTORS (PLATE & WACKERS)
| 8.7.2 | .11 Plate compactors (specify model)
|  | (a) Model_______ | hr | 8 | 450
| 8.7.2 | .12 Wackers (specify model)
|  | (a) Model_______ | hr | 8 | 450
CONCRETE MIXERS
B1.1.11 | 8.7.2 | .13 Concrete mixers (specify mixing volume)
|  | (a) Volume______liter (small, towable) | hr | 8 | 450
|  | (b) Volume______liter (medium) | hr | 8 | 800
COMPRESSORS
B1.1.12 | 8.7.2 | .14 Portable diesel compressors (specify capacity)
|  | (a) Capacity_____cfm (small) | hr | 8 | 450
|  | (b) Capacity_____cfm (medium) | hr | 8 | 650
|  | (c) Capacity_____cfm (large) | hr
WATERPUMPS
B1.1.13 | 8.7.2 | .15 Waterpump (specify capacity)
|  | (a) Capacity_____ liter/sec (small) | hr | 8
|  | (b) Capacity__10__ liter/sec (medium) | hr | 224 | 800
|  | (c) Capacity_____ liter/sec (large) | hr | 8
Total Carried Forward
C2.2-2-2
#REF!
SCHEDULE OF QUANTITIES
SCHEDULE 2 : DAYWORKS & PROVISIONAL SUMS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
WELDERS
B1.1.14 | 8.7.2 | .16 Welding unit (specify Ampere)
|  | (a) ______Amp (small) | hr | 8 | 150
|  | (b)______Amp (medium]) | hr | 8 | 300
|  | (c)______Amp (large) | hr | 8 | 450
GENERATORS
B1.1.15 | 8.7.2 | .17 Mobile generator set (specify kVA)
|  | (a)__11.5____kVA (small) | hr | 8 | 450
B1.1.16 |  | TRANSPORT (TRANSPORT COST TO AND FROM SITE)
Note : Distance shall be measured one way only (Tender rates shall include for transport in both directions to and from site)
| 8.7.3 | .1 Low bed
|  | (a) Low-bed (suitable for the largest piece of equipment above) | km | 6000 | 10
B1.2 | SANS 1200A | SCHEDULE 2.2 : SUMS STATED PROVISIONALLY BY THE ENGINEER
|  | Provisional sum for cost of material | Prov sum | 1 | 200000 | 200000
|  | Contractor's mark-up on material | % |  | 200000
Total Carried Forward To Summary

## Sche B2_n
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE B2 : TANK CLEANING, DEMOLITIONS & REPLACEMENT FENCING | SCHEDULE B1 : TANK CLEANING, DEMOLITIONS & REPLACEMENT FENCING | SCHEDULE B1 : TANK CLEANING, DEMOLITIONS & REPLACEMENT FENCING | SCHEDULE B1 : TANK CLEANING, DEMOLITIONS & REPLACEMENT FENCING
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B2 |  | SCHEDULE B2 : TANK CLEANING, DEMOLITIONS & REPLACEMENT FENCING
Drain, Clean & inspect
|  | Activated sludge reactor (BNRAS) | sum | 1
|  | Clarifier | sum | 1
|  | Chlorine Contact Tank (exist) | sum | 1
B2.1.1 |  | Demolition
B2.2 |  | Demolition of existing damaged concrete pallisade fence, 2.4m high | m3 | 140
B2.2.1 |  | Remove rubble from site to a designated dumping site | m3 | 140
Demolition at Inlet Works:
|  | Reinforced Concrete Demolitions: Demolish part of ex reinf concr inlet channel (at inlet and at grit channels for vortex chamber construction) | m3 | 7.3
|  | Demolish masonry: Remains of old screening area roof columns, brick upstand to inlet channel lip and part of inlet works building (above windows and above 1.9m height) | m3 | 5
Demolition of Small Building at Chlorination Tank
|  | Demolish Reinforced Concrete (RC): Small redundant building at chlorination tank | m³ | 1.25
|  | Demolish masonry: Breaking down and removing brickwork: one brick wall (230mm thk) | m2 | 23
Supply and Install New Security Fencing
Type 1 Fence (Concrete Palisade System):
|  | 2.4m high: Supply and install (complete, but excl. concrete to posts) | m | 633
|  | Provide Concrete to posts: Guide for each post: 0.5m x 0.5m x 0.5m (= 0.125m3 / post): Posts at 2m c/c | no | 318
|  | Supply and install Razer Coil Wire : 730mm dia, mid-way along fence | m | 633
|  | 730mm dia, at bottom of fence | m | 633
Type 2 Fence (Welded Mesh Medium Security):
|  | 2.4m high x medium security incl. spike at top railing Rate / m incl. excav, posts, supply install (excl. gates).Galvanised mesh 76mm x 25mm apperture | m | 1180
Supply and instll razer wire
|  | 730mm dia, at top of fence | m | 1180
|  | 730mm dia, at bottom of fence | m | 1180
Grade 25/ 19 Under-dig Concrete Protection
|  | 0.2m w x 0.1m deep x length: excavate, place and cure. All inclusive rate | m | 1180
|  | 2.4m high x 4m long; all inclusive | no | 7
|  | 2.4m high x1.2m wide; all inclusive | no | 1
Type 2 Fence: For Generator Area (Mains)
|  | 2.4m high x medium security incl. spike at top railing Rate / m incl. excav, posts, supply install (excl. gates). Galvanised mesh 76mm x 25mm apperture | m | 10
|  | 2.4m high x1.2m wide; all inclusive | no | 1
|  | 2.4m high x medium security incl. spike at top railing Rate / m incl. excav, posts, supply install (excl. gates).Galvanised mesh 76mm x 25mm apperture | m | 36.6
|  | 2.4m high x1.2m wide; all inclusive | no | 1
Type 2 Fence: For Generator Area (Back-up)
|  | 2.4m high x medium security incl. spike at top railing Rate / m incl. excav, posts, supply install (excl. gates).Galvanised mesh 76mm x 25mm apperture | m | 36.6
Total Carried Forward To Summary

## Sche B3_n
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE B3 : EARTHWORKS, PIPELINES AND ELECTRICAL CABLE DUCTS | SCHEDULE B2 : EARTHWORKS, PIPELINES AND ELECTRICAL CABLE DUCTS | SCHEDULE B2 : EARTHWORKS, PIPELINES AND ELECTRICAL CABLE DUCTS | SCHEDULE B2 : EARTHWORKS, PIPELINES AND ELECTRICAL CABLE DUCTS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B3 |  | SCHEDULE B3 : EARTHWORKS, PIPELINES AND ELECTRICAL CABLE DUCTS
Excavations
B3.1
|  | Trench Excavations - not exceeding 1.2m deep | m3 | 465
|  | Trench Excavations - not exceeding 2m deep (single pipe trenches) | m3 | 1040
|  | Trench Excavations - not exceeding 2m deep (multiple pipes in trench) | m3 | 412
|  | Excavations: For chambers and holes - not exceeding 2m deep | m3 | 13.5
|  | 110mm UPVC Pipe Cl34 (supply only) | m | 40
|  | Trench Excavations - not exceeding 1.5m deep | m3 | 19.2
|  | G7: Under floors, steps, pavings, etc. Roadworks. Compact to 93% / 100% (for SAND) MOD AASHTO | m3 | 5.2199
|  | Backfilling from on-site / stockpile to trenches, holes, etc. Compact to 98% MOD AASHTO unless otherwise indicated | m3 | 13.6
|  | Incl, Valves (DN50 x 2), scour valve, water meter & water meter chamber | sum | 1
|  | Water standpipe & tap installation complete for water re-use point of use | no | 10
|  | Import selected granular material (G7) and compact to 93% MOD AASHTO (100% for sand): 300mm thk | m3 | 4.05
|  | Spoil excavated material on site; 5km freehaul | m3 | 13.5
Pipe Trenches
Selected granular & fill material for pipe bedding:
|  | Import selected granular material (G7) and compact to 93% MOD AASHTO (100% for sand) | m3 | 142
|  | Backfilling from on-site / stockpile to trenches, holes, etc. Compact to 93% MOD AASHTO unless otherwise indicated | m3 | 315
|  | Spoil excavated material on site; 5km freehaul | m3 | 258
|  | Import selected granular material (G7) and compact to 93% MOD AASHTO (100% for sand) | m3 | 433
|  | Import selected fill material (G7) and compact to 93% MOD AASHTO (100% for sand) | m3 | 265
|  | Backfilling from on-site / stockpile to trenches, holes, etc. Compact to 98% MOD AASHTO unless otherwise indicated | m3 | 701
|  | Spoil excavated material on site; 5km freehaul | m3 | 751
Pipework
|  | Existing pipes: Secure and re-paint (BNRAS) | sum | 1
|  | Inspect and clean (swob / jet) underfloor influent and sludge draw-off pipework (Clarifier) | prov sum | 1 | 20000 | 20000
UPVC Pressure Pipe Class 6 - Buried cable duct
|  | 50mm OD UPVC Pressure Pipe Class 6 | m | 235
|  | 90mm OD UPVC Pressure Pipe Class 6 | m | 929
|  | 110mm OD UPVC Pressure Pipe Class 6 | m | 791
|  | 160mm OD UPVC Pressure Pipe Class 6 | m | 48.5
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
SCHEDULE B3 : EARTHWORKS, PIPELINES AND ELECTRICAL CABLE DUCTS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Supply, Install, and Fix Metallic Pipe Conduit for Elecrical Cables to existing above ground structure and test
|  | DN25, SS 304 Pipe, Tube (suppl and install to ex structure) | m | 0
|  | DN40, SS 304 Pipe, Tube (suppl and install to ex structure) | m | 0
|  | DN80, SS 304 Pipe, Tube (suppl and install to ex structure) | m | 0
|  | DN25 (32mm) GMS Pipe, threaded (supply & install, complete) | m | 11
|  | 40 mm GMS Pipe, threaded (supply & install, complete) | m | 20
|  | 50 mm GMS Pipe, threaded (supply & install, complete) | m | 0
|  | 80 mm GMS Pipe, threaded (supply & install, complete) | m | 123
For overhead PE cable conduit
|  | 90mm PE100 PN6.3 (supply and install to ex structure) | m | 0
UPVC Drainage Pipe Class 34
|  | 110mm UPVC Pipe Cl34 (supply only) | m | 99
|  | 160mm UPVC Pipe Cl34 (supply only) | m | 87
Water and Sewerage
|  | 90mm OD UPVC Pressure Pipe Class 6 | m | 208
|  | 160mm OD UPVC Pressure Pipe Class 6 | m | 17
|  | 250mm OD UPVC Pressure Pipe Class 6 | m | 35
UPVC Pressure Pipe Class 9
|  | 75mm OD UPVC Pressure Pipe Class 9 | m | 0
|  | 90mm OD UPVC Pressure Pipe Class 9 | m | 0
|  | 110mm OD UPVC Pressure Pipe Class 9 | m | 459
|  | 160mm OD UPVC Pressure Pipe Class 9 | m | 0
|  | 200mm OD UPVC Pressure Pipe Class 9 | m | 5
|  | 250mm OD UPVC Pressure Pipe Class 9 | m | 0
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
m
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
HDPE Pipes
PE100 Pressure Pipe Class 6 (PN6.3)
|  | 32mm PE100 PN6.3 (supply & lay in trench) | m | 137
|  | 40mm PE100 PN6.3 (supply & lay in trench) | m | 209.4
|  | 50mm PE100 PN6.3 (supply & lay in trench) | m | 8.5
|  | 63mm PE100 PN6.3 (supply & lay in trench) | m | 0
|  | 75mm PE100 PN6.3 (supply & lay in trench) | m | 0
|  | 90mm PE100 PN6.3 (supply & lay in trench) | m | 0
|  | 110mm PE100 PN6.3 (supply & lay in trench) | m | 53.4
PE100 Pressure Pipe Class 10
|  | 32mm PE100 PN10 (supply & lay in trench) | m | 2.3
|  | 40mm PE100 PN10 (supply & lay in trench) | m | 0
|  | 50mm PE100 PN10 (supply & lay in trench) | m | 198
|  | 75mm PE100 PN10 (supply & lay in trench) | m | 0
|  | 90mm PE100 PN10 (supply & lay in trench) | m | 70.2
|  | 225mm PE100 PN10 (supply & lay in trench) | m | 56
PE100 Pressure Pipe Class 12
Supply, install & test (excluding bedding, backfill, excavations)
|  | 32mm PE100 PN12.5 (supply & lay in trench) | m | 25
|  | 40mm PE100 PN12.5 (supply & lay in trench) | m | 0
|  | 50mm PE100 PN12.5 (supply & lay in trench) | m | 0
|  | 90mm PE100 PN12.5 (supply & lay in trench) | m | 542
|  | 110mm PE100 PN12.5 (supply & lay in trench) | m | 0
|  | 125mm PE100 PN12.5 (supply & lay in trench) | m | 47
Steel Pipe (SS)
Supply, Install, Fix to existing above ground structure and test
|  | DN80, SS 304 Pipe, Tube (supply and install, test, complete) | m | 3
|  | DN100, SS 304 Pipe, Tube (supply and install, test, complete) | m | 1.5
|  | DN150, SS 304 Pipe, Tube (supply and install, test, complete) | m | 0
Ductile Iron Sewer Pipe with Lining
Supply and install (excluding bedding, backfill, excavations)
|  | DN100 DI Sewer Pipe (PAM Saint Gobain, "Integral) or similar | m | 10
|  | DN300 DI Sewer Pipe (PAM Saint Gobain, "Integral) or similar | m | 27
|  | DN450 DI Sewer Pipe (PAM Saint Gobain, "Integral) or similar | m | 18
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
0
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Concrete Sewer Pipes
Supply and install (excluding bedding, backfill, excavations)
Concrete pipes: Sewer with sacrificial layer (Spigot & Socket, Class 50D)
|  | Concrete pipe culvert 300mm dia (class 50D), Spigot and socket, class B bedding | m | 104
|  | Concrete pipe culvert 375mm dia (class 50D), Spigot and socket, class B bedding | m | 10
|  | Concrete pipe culvert 450mm dia (class 50D), Spigot and socket, class B bedding | m | 66
|  | Concrete pipe culvert 525mm dia (class 50D), Spigot and socket, class B bedding | m | 0
|  | Concrete pipe culvert 600mm dia (class 50D), Spigot and socket, class B bedding | m | 0
|  | Concrete pipe culvert 675mm dia (class 50D), Spigot and socket, class B bedding | m | 0
Specials & Fittings
|  | Water standpipe & tap installation complete for water re-use point of use | no | 10
|  | Cable Draw-pit Chamber (750mm x 750mm x 0.8m deep) complete with secure lid & cable draw ropes | no | 34
|  | Install RSV Gate Valve, DN100 (with valve cap) - for WAS rising main with reticulation to sludge drying beds as per site layout drawing | no | 9
|  | Resilient Seat Gate Valve (RSV), DN 300, Flanged, Valve complete with Valve Cap [for Ponds - anticipated replacement] | no | 2
|  | Resilient Seal Gate Valve (RSV), DN 400, Flanged, Valve complete with Valve Cap [for Ponds - anticipated replacement] | no | 1
Replace local on-site sewer pipe replacement (building services, incl. guardhouse)
|  | 110mm UPVC Pipe Cl34 (supply only) | m | 40
|  | Trench Excavations - not exceeding 1.5m deep | m3 | 19.2
|  | G7: Under floors, steps, pavings, etc. Roadworks. Compact to 93% / 100% (for SAND) MOD AASHTO | m3 | 5.2199
|  | Backfilling from on-site / stockpile to trenches, holes, etc. Compact to 98% MOD AASHTO unless otherwise indicated | m3 | 13.6
|  | Incl, Valves (DN50 x 2), scour valve, water meter & water meter chamber | sum | 1
|  | Water standpipe & tap installation complete for water re-use point of use | no | 10
Soil & MaterialsTesting
| PSA7.9 | Compaction testing, soils testing by SANAS accredited laboratory as and when required by the Engineer | Prov sum | 1 | 50000 | 50000
|  | .10 Overheads, charges and profit on above | % |  | 50000
Water Quality Testing
| PSA7.9 | Testing -Water Quality sampling & Lab analysis by SANAS accredited laboratory as and when required by the Engineer | Prov sum | 1 | 50000 | 50000
|  | .10 Overheads, charges and profit on above | % |  | 50000
Total Carried Forward To Summary

## Sche B4_n
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE B4: BULK EARTHWORKS: SLUDGE DRYING BEDS & COMPOSTIING AREA | SCHEDULE B3: BULK EARTHWORKS: SLUDGE DRYING BEDS & COMPOSTIING AREA | SCHEDULE B3: BULK EARTHWORKS: SLUDGE DRYING BEDS & COMPOSTIING AREA | SCHEDULE B3: BULK EARTHWORKS: SLUDGE DRYING BEDS & COMPOSTIING AREA
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B4 |  | SCHEDULE B4: BULK EARTHWORKS: SLUDGE DRYING BEDS & COMPOSTIING AREA
|  | Cut and fill, for platforms | m3 | 3924
|  | Spoil remaining excavated material within 5km freehaul | m3 | 2927
|  | Rip and compact in-situ (0.15m thk) to 93% MOD AASHTO | m3 | 556
|  | G5: Under floors, steps, pavings, etc. Base course. Compact to 98% MOD AASHTO | m3 | 834
|  | G7: Under floors, steps, pavings, etc. Roadworks. Compact to 93% / 100% (for SAND) MOD AASHTO | m3 | 1668
|  | Hollow clay plaster brick: Apollo NFP Maxi Clay: 222 x 114 x 90 (for use in sludge drying bed media layer) | no | 9247
|  | Imported 9mm Stone for 100mm thk layer | m3 | 327
|  | Imported Course River Sand for 100mm thk layer | m3 | 327
|  | Imported 13mm Stone (for filter drain) | m3 | 73
|  | Geotextile: A2 Bidim for filter drain | m2 | 908
|  | Slotted Drain Pipe, 110mm OD Kaytech Kaypipe or similar approved | m | 560
New concrete works for rectangular channels at Inlet Works (new and raising of upstand for existing)
|  | Inlet works channels: Readymix - Blinding - Grade 15 / 20 | m3 | 0.8
|  | Inlet works channels: Readymix - Grade 30/19 - Floor | m3 | 3.1
|  | Inlet works channels: Not reinforced (with pump support) | m3 | 7
|  | High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 0.98
|  | Smooth Formwork (Degree of accuracy I): To walls | m2 | 96
|  | Finishing top surfaces of concrete smooth with a steel float: | m2 | 9
|  | Wire brushing of concrete surfaces to expose aggregate: Walls, floors | m2 | 4.163
|  | Drill holes for re-bar & apply epoxy grout to hole | no | 78
|  | Construction Joint: Inlet works Channel: Sikadur Combiflex SG20 P1000 (2mm thk tape x 200mm width) | no of 25m rolls | 3
|  | Construction Joint: Sika PVC Waterbar AR-25, 250mm wide (or similar approved) | no of 15m rolls | 4
|  | Concrete strength testing: Inlet works channels. Concrete cubes for crush testing; all inclusive rate: Making and testing 150 x 150 x 150mm concrete strength test cube | no of | 6
Modifications & Additions to existing Inlet Channels
Concrete Repairs & Waterproofing (Existing Inlet Channels)
|  | Grit Blasting to prepare concrete for repairs | m2 | 126
|  | Cementitious flexible rendering coat with waterproofing capability to fill blowholes & honeycombing / spalling; making level. Saint Gobain ABE Durarep (or similar) applied in min 2 coats | no of 15 kg bags | 34
|  | Apply cementitious flexible waterproofing slurry (Saint Gobain ABE Durarep or similar) in min 2 coats | no of 15 kg bags | 34
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B4: BULK EARTHWORKS: SLUDGE DRYING BEDS & COMPOSTIING AREA | SCHEDULE B3: BULK EARTHWORKS: SLUDGE DRYING BEDS & COMPOSTIING AREA | SCHEDULE B3: BULK EARTHWORKS: SLUDGE DRYING BEDS & COMPOSTIING AREA | SCHEDULE B3: BULK EARTHWORKS: SLUDGE DRYING BEDS & COMPOSTIING AREA
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Addition of New Circular Vortex-type Degritting Chambers (x 2 no) & overhead walkway @ Existing Inlet Works
Readymix: sulphate resistant with additional cement content for water retaining (Vortex chambers & overhead walkway):
|  | Blinding layer - grade 15/19 | m3 | 0.5
|  | Readymix - Grade 30/19 - Footings / Floor slab | m3 | 4.6
|  | Readymix - Grade 30/19 - Walls | m3 | 13
|  | Readymix - Grade 30/19 - Roof slab | m3 | 1.9
|  | New Vortex Chambers (Inlet works): High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 1.03
|  | Smooth Formwork (Degree of accuracy I): To walls | m2 | 77.3
|  | Smooth Formwork (Degree of accuracy I): To roof or slab soffit: slabs propped up exceeding 1,5m and not exceeding 3,5m high | m2 | 8.5
|  | Finishing top surfaces of concrete smooth with a steel float: | m2 | 10
|  | Concrete strength testing: Inlet works channels. Concrete cubes for crush testing; all inclusive rate: Making and testing 150 x 150 x 150mm concrete strength test cube | no of | 9
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 0
|  | 50 x 50 x 5mm L-section frame in lengths not exceeding 13m welded to mentis grating (mentis grating measured elsewhere) including 14mm diameter holes for bolts | m | 0
Total Carried Forward To Summary

## Sche B5_n
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE B5: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B5 |  | SCHEDULE B5: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
Demolitions
|  | Remove rubble from site to a designated dumping site | m3 | 38.05
Cleaning of channels
|  | Remove silt, mud, debris from Wastewater tank / vessel , dry and dispose to registered landfill site | m3 | 14.6
Site clearance
|  | Remove topsoil to nominal depth of 100mm and stockpile | m3 | 150
Excavations: For all works at Inlet works
|  | Excavate in all materials (other tha hard and boulder) and spoil incl. 5km freehaul | m3 | 138
|  | Excavations: Extra over: Hard rock | m3 | 1
|  | Excavations: Extra over: Boulders class A | m3 | 2
Earthworks
|  | Rip and compact in-situ (0.1m thk) to 93% MOD AASHTO | m3 | 42
|  | Import G7 amd compact to 95% MOD AASHTO | m3 | 14
|  | (a) Excavate for canopy base footings in all materials to depth specified in drawings | m3 | 6.6
|  | Backfilling from on-site / stockpile to trenches, holes, etc. Compact to 93% MOD AASHTO unless otherwise indicated | m3 | 2
Structural Concrete
Inlet Works: Structural foundation concrete for washwater pump enclosure
|  | Install vertical flow straightener bars upstream of existing flume location | sum | 1
|  | Partial demolition and rebuild of existing parshall flume to improve accuracy | sum | 1
|  | Concrete base slab (0.5m x 0.5m x 0.1m with 1m high enclosed metal kios for ultrasonic converted | sum | 1
Roadworks
|  | Remove existing brick paving and stockpile for re-use | m2 | 51
|  | Relay existing clay brick paving from on-site stockpile; herringbone arrangement | m2 | 33
|  | Supply and place jointing sand and compact with plate compactor | m2 | 33
|  | In-situ concrete grade 30 / 19 for edge to paving header course | m3 | 0.5625
Building works
|  | Stippled plaster on brickwork: On walls and window cills (Interior & Exterior - Entire surface Area) | m2 | 92
|  | New steel door / roller shutter | no | 1
|  | New geyser: Complete installation, including drip tray, geyser and fittings in compliance with SANS 10254. Geyser type: Kwikot Superline 400 Dual (DSG-100-5, 100L ) or similar approved | no | 1
|  | New windows and burglar bars | sum | 1
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B5: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Structural Steelwork
Supply and Fabrication
|  | Preparation of shop detail drawings | Sum | 1
Supply and fabrication of steel work for (lengths measured from centre of all joints):
|  | (1) Columns 6 of (254x146x37 I Section) | t | 1.001
|  | (2) Beams 2 of (254x146x37 I Section) | t | 0.363
|  | (3) Gantry Beam 1 of (IPE 200 I Section) | t | 0.0957
|  | (4) Rafters 6 of (254x146x37 I Section) | t | 0.5533
|  | (5) Top rail 4 of (76.2x3.0 Circular Hallow Section) | t | 0.10069
|  | (6) Bracing with Equal Angles 70x70x6mm with 2-M12 Grade 8.8 bolts per connection | t | 0.4158
|  | (7) Sag bras 50x50x3mm Equal Angles | t | 0.020779
|  | (8) Purlins 100x50x20x2.5 lipped channel | t | 0.253
|  | (9) Sheeting rails (side cladding) 100x50x20x2.5 lipped channel | t | 0.3212
|  | (10) Base plates 450x350x18mm (6 OF) | t | 0.1474
|  | 0.5mm IBR Sheeting | m2 | 85.86
Delivery to Site
|  | Normal delivery: | t | 3.2719
Erection on site
|  | (1) Columns 6 of (254x146x37 I Section) | t | 1.001
|  | (2) Beams 2 of (254x146x37 I Section) | t | 0.363
|  | (3) Gantry Beam 1 of (IPE 200 I Section) | t | 0.0957
|  | (4) Rafters 6 of (254x146x37 I Section) | t | 0.5533
|  | (5) Top rail 4 of (76.2x3.0 Circular Hallow Section) | t | 0.10069
|  | (6) Bracing with Equal Angles 70x70x6mm with 2-M12 Grade 8.8 bolts per connection | t | 0.4158
|  | (7) Sag bras 50x50x3mm Equal Angles | t | 0.020779
|  | (8) Purlins 100x50x20x2.5 lipped channel | t | 0.253
|  | (9) Sheeting rails (side cladding) 100x50x20x2.5 lipped channel | t | 0.3212
|  | (10) Base plates 450x350x18mm (6 OF) | t | 0.1474
Holding down (HD) bolts
|  | (a) M16 HD bolts (400mm long) (4 in 6 baseplates) | No | 24
|  | (b) 40x40x3mm Equal angles fixed to bottom of HD bolts (450mm long) (12 of) | t | 0.011108
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B5: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
CORROSION PROTECTION OF STRUCTURAL STEELWORK (INLET WORKS; SCREENINGS AREA ROOF)
Corrosion Protection (Will be measured and paid extra-over items listed in accordance with SABS 1200 HC)
Corrosion Protection of Structural Steelwork
Steel coating system: All steel to receive a Coated System, consisting of a HDG coating, conforming to the below specifications. • All steel to be HDG (Hot Dipped Galvanised) to SANS 121 with min thickness of 85 micrometres; Bolts to be HDG with min 55 micrograms Zink coating. Electroplated bolts will not be accepted. • Protective treatment, other than site-applied coatings, shall be applied under factory conditions in an enclosed shop.
Surface dressing and repairs at place of fabrication
Extra-over item D3 (8.3.1.2 - Supply and fabrication of steel work:
|  | All sections | t | 3.2719
|  | Transport | t | 3.2719
Surface preparation and coating application
|  | (a) In the shop | t | 3.2719
|  | (a) On site | t | 3.2719
Establishment on site for corrosion protection:
|  | Remedial work to repair any damaged HDG coating system on site | Sum | 1
CONCRETE (STRUCTURAL): INLET WORKS; SCREENINGS AREA ROOF
Concrete (Structural)
FORMWORK ITEMS
REINFORCEMENT ITEMS
|  | Reinforcing bars: All Diameters | t | 0.322
CONCRETE ITEMS
Pre-mixed concrete to be used. Mix design from supplier to be provided to Engineer at least 14 days prior to casting on site. Minimum strength after 28 days as specified. Complete. All quantites are provisional.
|  | Blinding layer of 25mm thick concrete, Class 15/19, placed for tower foundation. | m3 | 0.15
Concrete, Class 30/19, with: reinforcing cover of 50mm where applicable reinforcing overlap of mibnimum 50 x bar diameter no concrete cast without the approval of the engineer all top edges of concrete above ground level must have a 20 mm chamfer at 45° for the following items:
|  | (a) Column bases to specified depth (Class 30MPa / 19mm) | m3 | 6.6
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B5: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
GROUTING
(a) Under base plates:
|  | (1) 25mm Non-shrink grout under all baseplates (Flowable 30MPa) | m3 | 0.026
Reinf Con Slabs : Inlet Works
|  | Inlet works: various floor slabs: Readymix - Grade 30/19 - Footings / Floor slab | m3 | 13.4
|  | Inlet works: various floor slabs: High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 1.1
|  | Concrete finish: Finishing top surfaces of concrete smooth with a steel float: | m2 | 85
|  | Smooth Formwork (Degree of accuracy I): To slab | m2 | 8
|  | Concrete strength testing: Inlet works channels. Concrete cubes for crush testing; all inclusive rate: Making and testing 150 x 150 x 150mm concrete strength test cube | no of | 12
Inlet Works: Structural Concrete
|  | Inlet works: concrete walkways: Readymix - Grade 40/19 - Overhead slab | m3 | 1.7
|  | Inlet works: conc walkways: High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 0.15
|  | Concrete finish: Finishing top surfaces of concrete smooth with a steel float: | m2 | 5
|  | Smooth Formwork (Degree of accuracy I): To walls | m2 | 5.2
|  | Smooth Formwork (Degree of accuracy I): To roof or slab soffit: slabs propped up exceeding 1,5m and not exceeding 3,5m high | m2 | 4.6
|  | Concrete strength testing: new concr access walkways. Concrete cubes for crush testing; all inclusive rate: Making and testing 150 x 150 x 150mm concrete strength test cube | no of | 3
Inlet Works: Structural foundation concrete for washwater pump enclosure
|  | Readymix - Grade 30/19 - Footings / Floor slab | m3 | 1.2
|  | High Tensile Steel: Inlet works: conc walkways: High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 0.1
|  | Grade 30 / 19: Washwater pump enclosure finish: Finishing top surfaces of concrete smooth with a wood float: (max tolerance of 3mm) | m2 | 4.7
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B5: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Refurbish Existing Inlet Works Building
|  | Repair existing interior; including new basic furniture | sum | 1
|  | Brickwork of NFP bricks in Class II mortar: one brick wall (230mm) | m2 | 10
|  | Readymix - Grade 30/19 - Roof slab (175mm thk) | m3 | 4.3
|  | Readymix - Grade 30/19 - Footings / Floor slab (80mm thk; cast on existing) | m3 | 1.5
|  | Inlet works building refurb: roof slab and floor slab High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 0.54
|  | Finishing top surfaces of concrete smooth with a steel float: | m2 | 25
|  | Smooth Formwork (Degree of accuracy I): To roof or slab soffit: slabs propped up exceeding 1,5m and not exceeding 3,5m high | m2 | 25
|  | Wire brushing of concrete surfaces to expose aggregate: Walls, floors | m2 | 18
|  | On floors in patches | m2 | 18
|  | Certificate of Compliance for plumbing & drainage installation for Office Building | no | 1
Testing
|  | Concrete cube strength testing by commercial laboratory, including the evaluation of concrete characteristics as specified by the Engineer. | Prov sum | 1 | 30000 | 30000
Total Carried Forward To Summary

## Sche B6_n
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE B6: SLUDGE DRYING BEDS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B5: SLUDGE DRYING BEDS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B5: SLUDGE DRYING BEDS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B5: SLUDGE DRYING BEDS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B6 |  | SCHEDULE B6: SLUDGE DRYING BEDS: CONCRETE WORKS (STRUCTURAL)
|  | Blinding layer - grade 15/19: Footings & Floor | m3 | 178
|  | Concrete grade 35 / 19: footings, floor and ramps - sulphate resistant | m3 | 666
|  | Concrete grade 35 / 19: walls - sulphate resistant | m3 | 167
|  | High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 73.3
|  | Finishing top surfaces of concrete smooth with a wood float: (max tolerance of 3mm) | m2 | 3837
|  | Finishing top surfaces of concrete smooth with a steel float: | m2 | 1409
|  | Rough Formwork (Degree of accuracy II): To base | m2 | 310
|  | Smooth Formwork (Degree of accuracy I): To walls / vertical faces | m2 | 1409
|  | Making and testing 150 x 150 x 150mm concrete strength test cube | no | 47
|  | 20mm chamfer to edge | m | 691
Concrete Joints: Waterproofing Work
Horizontal Construction Joints (walls)
|  | Swellable Joint Sealing Profile: Sikaswell A-2010 M Yellow (units: box with 6 no x 10m) | no of boxes with 6 x 10m strips | 12
|  | Adhesive for Sikaswell Joint Sealing Profile: SikaSwell S-2 (Oxyd Red-Up) - Approx consumption: 6m / 600ml kit | no of 600ml kits | 119
|  | Sikadur Combiflex SG20 P1000 (2mm thk tape x 200mm width) | no of 25m rolls | 102
|  | Sika Waterbar AR-25, 250mm wide (or similar approved) | no of 15m rolls | 125
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 3.36
|  | 50 x 50 x 5mm L-section frame in lengths not exceeding 13m welded to mentis grating (mentis grating measured elsewhere) including 14mm diameter holes for bolts | m | 20.44
Bio-friendly sludge handling area
New concrete slab (200mm thk) near entrance
|  | General Readymix - Grade 35/19 - Footings | m3 | 14.5
|  | Readymix: Grade 35 / 19: Floor slab, 200mm thk x 24m x 10m (excl. reinf steel) | m3 | 44.5
|  | High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 4.5
|  | Finishing top surfaces of concrete smooth with a wood float: (max tolerance of 3mm) | m2 | 223
|  | Rough Formwork (Degree of accuracy II): To walls / vertical faces | m2 | 14
|  | Making and testing 150 x 150 x 150mm concrete strength test cube | no | 9
|  | Brickwork of NFX bricks (14 MPa nominal compressive strength) in Class I mortar: one brick wall (230mm) | m2 | 61.5
|  | Brickwork of NFP bricks in Class II mortar: one brick wall (230mm) | m2 | 93
|  | Brickforce, 150mm wide x 2.8mm x 20m roll | per 20 m roll | 47
Total Carried Forward To Summary

## Sche B7_n
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
SCHEDULE B7: MODIFICATIONS & REPAIRS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B7 |  | SCHEDULE B7: MODIFICATIONS & REPAIRS: CONCRETE WORKS (STRUCTURAL)
Earthworks
RAS & WAS Chamber
|  | Cut to spoil incl. 5km freehaul; Intermediate excavation | m3 | 5
|  | Import selected granular material (G7) and compact to 93% MOD AASHTO (100% for sand) | m3 | 1.4
|  | Rip and compact in-situ (0.1m thk) to 93% MOD AASHTO | m3 | 1
Cleaning of existing Manholes & Chambers
|  | Remove concrete fence post and rubble from manhole (MH6) | no | 1
|  | Minor works: Drain & clean interior of manhole from silt and rubbish | no | 31
Replace existing manhole covers and secure
|  | Replace 600mm diameter ductile iron lid and frame with secure lockable DI cover to suit existing opening. Cast 80mm grade 25 / 19 concrete to top of frame | no | 2
|  | Replace 560mm MD concrete lid (560mm circular diameter) with new concrete lid (like for like) | no | 1
|  | Secure existing frame with 80mm thk grade 30 / 19 concrete to top of frame with smooth steel float finish: 2 no of manholes | m3 | 0.47214
Replace plastic covers to manholes
|  | Light Duty plastic cover and frame to 1.5m x 1.5m opening (underlying GMS grid & frame measured elsewhere) | no | 10
|  | Light Duty plastic cover and frame to 1.0m x 1.0m opening (underlying GMS grid & frame measured elsewhere) | no | 2
|  | Light Duty plastic cover and frame to 1.0m x 1.5m opening (underlying GMS grid & frame measured elsewhere) | no | 1
|  | RAS valve chamber: Light Duty plastic cover and frame to 1.0m x 1.5m opening (underlying GMS grid & frame measured elsewhere) | no | 3
Re-build existing manholes (changes to invert floor level & pipe openings, benching) with manhole up to 3m depth
Re-build existing manholes (changes to invert floor level & pipe openings, benching) with manhole up to 3m depth
|  | For manhole up to DN1500 size PCC Manhole (existing) | no | 3
Install new manholes: For Sludge Drying Beds; Filtrate Pipe
|  | Install new manhole: DN 1000 PCC circular manhole complete with cover and lid up to 1.5m depth | no | 17
|  | Install new manholes: For Sludge Drying Beds; New scum removal pipeline (Imhoff Tank to Sludge Drying Beds) | no
|  | Install new manhole: DN 1000 PCC circular manhole complete with cover and lid up to 1.5m depth | no | 6
Install new manholes: For Clarifier Influent Control Valve
|  | Install new manhole: DN 1000 PCC circular manhole complete with cover and lid up to 2.2m depth | no | 1
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B7: MODIFICATIONS & REPAIRS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Install new manholes: For WAS Rising Main and BNRAS high-flow by-pass sewer
|  | Install new manhole: DN 1000 PCC circular manhole complete with cover and lid up to 1.0m depth | no | 4
|  | Rectangular valve chamber complete (for WAS rising main flow-split control, valve chamber): 1.5m L x 0.9m wide x 0.9m deep. Complete with lockable plastic lids, excluding pipe fittings | no | 1
New Concrete Works & Modifications
Concrete & Steel
|  | General Readymix - Grade 30/19 - Footings / Floor slab | m3 | 6
|  | High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 0.45
|  | Rough Formwork (Degree of accuracy II): To walls / vertical faces | m2 | 24
|  | Finishing top surfaces of concrete smooth with a steel float: | m2 | 6
|  | Making and testing 150 x 150 x 150mm concrete strength test cube | no | 3
Modifications to Clarifier Outlet Chamber for Scum Entrapment & Effluent Discharge
|  | Readymix - Grade 30/19: for repair of steps & smaller wall members | m3 | 2
|  | High Tensile Steel Reinforcement: Wall. | t | 0.22
|  | Finishing top surfaces of concrete smooth with a steel float: | m2 | 3
|  | Smooth Formwork (Degree of accuracy I): To walls (internal) | m2 | 8
CONCRETE REPAIRS
Chlorine Contact Tank: Repairs
|  | Grit Blasting to prepare concrete for repairs | m2 | 0
|  | Cementitious flexible rendering coat with waterproofing capability to fill blowholes & honeycombing / spalling; making level. Saint Gobain ABE Durarep (or similar) applied in min 2 coats | m2 | 0
|  | Apply cementitious flexible waterproofing slurry (Saint Gobain ABE Durarep or similar) in min 2 coats | m2 | 0
|  | Crack repair (prepare, supply and install) | m | 0
Clarifier Tank (SST): Repairs
|  | Grit Blasting to prepare concrete for repairs | m2 | 729
|  | Cementitious flexible rendering coat with waterproofing capability to fill blowholes & honeycombing / spalling; making level. Saint Gobain ABE Durarep (or similar) applied in min 2 coats | no of 15 kg bags | 195
|  | Apply cementitious flexible waterproofing slurry (Saint Gobain ABE Durarep or similar) in min 2 coats | no of 15 kg bags | 195
|  | Crack repair (prepare, supply and install) | m | 30
Concrete Repairs: RAS & WAS Chambers
|  | Grit Blasting to prepare concrete for repairs | m2 | 21
|  | Cementitious flexible rendering coat with waterproofing capability to fill blowholes & honeycombing / spalling; making level. Saint Gobain ABE Durarep (or similar) applied in min 2 coats | no of 15 kg bags | 6
|  | Apply cementitious flexible waterproofing slurry (Saint Gobain ABE Durarep or similar) in min 2 coats | no of 15 kg bags | 6
|  | Crack repair (prepare, supply and install) | m | 3
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B7: MODIFICATIONS & REPAIRS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Bio-Filter
|  | Grit Blasting to prepare concrete for repairs | m2 | 1355
|  | Cementitious flexible rendering coat with waterproofing capability to fill blowholes & honeycombing / spalling; making level. Saint Gobain ABE Durarep (or similar) applied in min 2 coats | no of 15 kg bags | 362
|  | Apply cementitious flexible waterproofing slurry (Saint Gobain ABE Durarep or similar) in min 2 coats | no of 15 kg bags | 353
Activated Sludge (BNRAS)
|  | Grit Blasting to prepare concrete for repairs | m2 | 2755
|  | Cementitious flexible rendering coat with waterproofing capability to fill blowholes & honeycombing / spalling; making level. Saint Gobain ABE Durarep (or similar) applied in min 2 coats | no of 15 kg bags | 735
|  | Apply cementitious flexible waterproofing slurry (Saint Gobain ABE Durarep or similar) in min 2 coats | no of 15 kg bags | 735
|  | Crack repair (supply and install) | m | 40
|  | Demolish RC at BNRAS: Minor: for concrete step /similar repairs | m³ | 1.5
|  | With additional cement content for water retaining Not reinforced (with pump support) -- repair of steps & smaller wall members | m3 | 1.5
|  | Grade 30/19 Concrete: Steps | m3 | 1.5
|  | Finishing top surfaces of concrete smooth with a steel float: | m2 | 5
|  | Smooth Formwork (Degree of accuracy I): To walls | m2 | 1
|  | Smooth Formwork (Degree of accuracy I): To roof or slab soffit: slabs propped up exceeding 1,5m and not exceeding 3,5m high | m2 | 1
Imhoff Tank
|  | Grit Blasting to prepare concrete for repairs | m2 | 222
|  | Cementitious flexible rendering coat with waterproofing capability to fill blowholes & honeycombing / spalling; making level. Saint Gobain ABE Durarep (or similar) applied in min 2 coats | no of 15 kg bags | 60
|  | Apply cementitious flexible waterproofing slurry (Saint Gobain ABE Durarep or similar) in min 2 coats | no of 15 kg bags | 60
|  | Crack repair (supply and install) | m | 16
Water re-use System for Maintenance
|  | Concrete foundations and floor: Measured as part of inlet works (see further above in bill) | m3 | n/a
|  | Mobile Hire Crane - to re-position skew access slab for pond no 3 outlet structure | day | 1
|  | Coffer dam structure and de-watering for work to install new abstraction manhole: tempary works | sum | 1
Transformer sub-station building
|  | Ready mix -grade 30/19 Not reinforced | m3 | 12.3
|  | Steel Reinf- Footing 90 kg / m3 | m3 | 0
|  | Steel Reinf - Floor 80 kg / m3 | m3 | 12.3
Diesel Generator, Civils
|  | Ready mix -grade 30/19 Not reinforced | m3 | 2.94
|  | 75 kg / m3 | m3 | 2.94
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B7: MODIFICATIONS & REPAIRS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Diesel Fuel Tank Storage Structure
|  | Blinding layer - grade 15/19 | m³ | 1.2414
|  | Readymix - Grade 30/19 - Walls | m3 | 9
|  | Steel Reinf: Roof | m3 | 1.7769
|  | Steel Reinf: Footing / Floor | m3 | 2.6654
|  | Steel Reinf: Wall | m3 | 4.7748
New Security Office at front gate (dwg 10909001-0504)
|  | Surface blinding under footings: 50mm thk | m3 | 0.5
|  | Readymix - Grade 30/19 - Footings / Floor slab | m3 | 4.8
|  | Readymix - Grade 30/19 - Roof slab | m3 | 2.1
|  | High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 0.55
|  | Finishing top surfaces of concrete smooth with a wood float: (max tolerance of 3mm) | m2 | 13
|  | Finishing top surfaces of concrete smooth with a steel float: | m2 | 18.5
|  | Smooth Formwork (Degree of accuracy I): To roof or slab soffit: slabs propped up exceeding 1,5m and not exceeding 3,5m high | m2 | 7
|  | Smooth Formwork (Degree of accuracy I): To walls / vertical faces | m2 | 3
|  | Apron: Finishing top surfaces of concrete smooth with a wood float: (max tolerance of 3mm) | m2 | 1.2
|  | Brickwork of NFX bricks (14 MPa nominal compressive strength) in Class I mortar: one brick wall (230mm): 800mm high | m2 | 8
|  | Brickwork of NFP bricks in Class II mortar: one brick wall (230mm): average 2400mm high | m2 | 27
|  | Brickforce, 150mm wide x 2.8mm x 20m roll | per 20 m roll | 10
|  | Lintels: 1.8m long x 150mm wide | no | 3
|  | Lintels: 2.4m long x 150mm wide | no | 2
|  | 2 layers: 3-ply malthoid for wall joint: 225mm wide x 20m roll | m | 12
|  | 0.58mm thk steel plate for wall joint (to soffit of roof): per m2 | m2 | 3
|  | Air Brick: 390 x 190 x 50mm Clay vermin proof air brick (to conform to drawings / specifications) | no | 2
Total Carried Forward To Summary
Note on D102: George Muller: Iqbal to verify product; could also use m3 as unit

## Sche B8_n
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE B8: INTERAL ACCESS ROAD AND DRAINAGE | SCHEDULE B7: INTERAL ACCESS ROAD AND DRAINAGE | SCHEDULE B7: INTERAL ACCESS ROAD AND DRAINAGE | SCHEDULE B7: INTERAL ACCESS ROAD AND DRAINAGE
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B8 |  | SCHEDULE B8: INTERAL ACCESS ROAD AND DRAINAGE
|  | Cut to spoil incl. 5km freehaul; Intermediate excavation | m3 | 1068
Roadbed
|  | Rip and compact in-situ (0.15m thk) to 93% MOD AASHTO For area under concrete slab and for turning area. Total area: 29m x 24m | m3 | 46
|  | Import G6: for road works from Commercial source & compact to 95% MOD AASHTO | m3 | 68
|  | Import selected granular material (G7) and compact to 93% MOD AASHTO (100% for sand) | m3 | 68
Topsoil & Excavation
|  | Stripping average 150mm thick layer of top soil and stockpiling on site for re-use of cut soil | m² | 588
|  | Cut 400mm depth and spoil as directed by Engineer incl. 5km freehaul; Soft excavation | m3 | 979
Layerworks
|  | Roadbed: Rip and compact in-situ (0.1m thk) to 93% MOD AASHTO | m3 | 392
|  | Import G8 and compact: Roadworks. Compact to 93% / 100% (for SAND) MOD AASHTO: 0.45m thk | m3 | 588
|  | Import G7 and compact: Roadworks. Compact to 93% / 100% (for SAND) MOD AASHTO: 0.45m thk | m3 | 1176
|  | Import and compact G6: for road works. Compact to 95% MOD AASHTO: 0.15m thk | m3 | 588
Stormwater (roads)
|  | Excavate for open drains; all materials: ave 350mm deep x 500mm wide | m3 | 186.725
|  | Trench Excavations - not exceeding 2m deep | m3 | 30
|  | 300mm Conc Pipe (class 100 D) for road crossing laid in and including trenches not exceeding 1m deep | m | 30
|  | Backfilling from on-site / stockpile to trenches, holes, etc. Compact to 93% MOD AASHTO unless otherwise indicated | m3 | 27
|  | Concrete grade 20 / 19 (see detail roads drawing 10909001-0300) | m3 | 4.8
|  | High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 0.384
Total Carried Forward To Summary

## Sche B9_n
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE B9: BIO-FILTER: RE-BUILD | SCHEDULE B8: BIO-FILTER: RE-BUILD | SCHEDULE B8: BIO-FILTER: RE-BUILD | SCHEDULE B8: BIO-FILTER: RE-BUILD
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B9 |  | SCHEDULE B9: BIO-FILTER: RE-BUILD
Imhoff Tank
|  | Grit Blasting to prepare concrete for repairs | m2 | 222
|  | Cementitious flexible rendering coat with waterproofing capability to fill blowholes & honeycombing / spalling; making level. Saint Gobain ABE Durarep (or similar) applied in min 2 coats | no of 15 kg bags | 60
|  | Apply cementitious flexible waterproofing slurry (Saint Gobain ABE Durarep or similar) in min 2 coats | no of 15 kg bags | 60
|  | Crack repair (supply and install) | m | 16
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 5.1
|  | 50 x 50 x 5mm L-section frame in lengths not exceeding 13m welded to mentis grating (mentis grating measured elsewhere) including 14mm diameter holes for bolts | m | 4.36
BioFilter inlet chamber (old Syphon Chamber)
|  | Remove silt, mud, debris from Wastewater tank / vessel , dry and dispose to registered landfill site | m3 | 1
|  | Install new GMS overflow weir and syphon pipework | sum | 1
|  | Grit Blasting to prepare concrete for repairs | m2 | 40
|  | Cementitious flexible rendering coat with waterproofing capability to fill blowholes & honeycombing / spalling; making level. Saint Gobain ABE Durarep (or similar) applied in min 2 coats | no of 15 kg bags | 11
|  | Apply cementitious flexible waterproofing slurry (Saint Gobain ABE Durarep or similar) in min 2 coats | no of 15 kg bags | 11
|  | Crack repair (supply and install) | m | 2
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 4
|  | 50 x 50 x 5mm L-section frame in lengths not exceeding 13m welded to mentis grating (mentis grating measured elsewhere) including 14mm diameter holes for bolts | m | 13.1
Flow Control Chamber to BNRAS:
|  | Palmer Bowlus Type Flow Meter - for DN300 pipe, complete with stubs (PVC material) | no | 1
|  | Grade 30 / 19 Concrete work to chamber floor to accommodate new flow meter | m3 | 1
|  | High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 0.1
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B9: BIO-FILTER: RE-BUILD | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Biofilter (Trickling Filter)
|  | Remove the existing media an place in stockpile near bio-filter for sieving and re-use (sieving and re-use construction measured elsewhere) | m3 | 3695
|  | Sieve and group removed media into 5 no of size ranges (40mm size, 50mm size, 63mm size, 75mm size and 100mm size) | m3 | 3203
|  | Re-use existing sieved media and install in respective layers | m3 | 3203
|  | Import and install replacement media to make up shortfall: average 40mm size stone | m3 | 65
|  | Import and install replacement media to make up shortfall: average 50mm size stone | m3 | 71
|  | Import and install replacement media to make up shortfall: average 63mm size stone | m3 | 73
|  | Import and install replacement media to make up shortfall: average 75mm size stone | m3 | 74
|  | Import and install replacement media to make up shortfall: average 100mm size stone | m3 | 75
|  | Supply and install dish-shaped rainwater channel (PCC - W1) to top of bio-filter and use concrete mortar to fix in place | m | 56
|  | Improve drainage to earth embankment Repair overflow / gutter to top of structure | sum | 1
|  | Remove Loffenstein L300 blocks and set-aside for re-use | no of | 4807
|  | Rebuild Löffenstein wall @ 85 deg incline - re-using existing L300 blocks | no of | 4127
|  | Supply, deliver and rebuild Löffenstein wall @ 85 deg incline - using NEW L300 blocks | no of | 410
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 1.4
|  | 50 x 50 x 5mm L-section frame in lengths not exceeding 13m welded to mentis grating (mentis grating measured elsewhere) including 14mm diameter holes for bolts | m | 4.2
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 24
|  | 50 x 50 x 5mm L-section frame in lengths not exceeding 13m welded to mentis grating (mentis grating measured elsewhere) including 14mm diameter holes for bolts | m | 6.67
Total Carried Forward To Summary

## Sche B10_
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE B10: BUILDING WORK: REFURB, RE-BUILD AND NEW (STRUCTURAL) | SCHEDULE B9: BUILDING WORK: REFURB, RE-BUILD AND NEW (STRUCTURAL) | SCHEDULE B9: BUILDING WORK: REFURB, RE-BUILD AND NEW (STRUCTURAL) | SCHEDULE B9: BUILDING WORK: REFURB, RE-BUILD AND NEW (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B10 |  | SCHEDULE B10: BUILDING WORK: REFURB, RE-BUILD AND NEW (STRUCTURAL)
Flow Meter Improvements (Civils Only)
|  | Concrete base slab (0.8m x 0.8m x 0.3m for ultrasonic clamp-on flow meter's steel mesh enclosed box (see item below). | m3 | 0.192
|  | Steel enclosed mesh and frame (high security) to enclose pipe section and ultrasonic clamp-on flow meter | sum | 1
MCC Building
|  | Refurbish existing interior: paint, windows, glazing | prov sum | 1 | 60000 | 60000
|  | Roller shutter door + outer protection | no | 1
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 4.9
|  | 50 x 50 x 5mm L-section frame in lengths not exceeding 13m welded to mentis grating (mentis grating measured elsewhere) including 14mm diameter holes for bolts | m | 0
Rebuild Store Room
|  | Blinding layer - grade 15/20 | m3 | 0.62
|  | Cement plaster steel trowelled on concrete: on interior walls | m2 | 41
|  | Steel droor & frame complete (Robmeg or similar): 890 x 2000mm | no | 2
|  | Heavy duty, high security, roller shutter door, complete with lock: size: 0.9m x 2m opening | no | 2
|  | Interior: Install HD Steel angle supports & pine shelving to two no of walls. [Provisional sum on basis of contractor design] | prov sum | 1 | 10000 | 10000
|  | Brickwork of NFX bricks (14 MPa nominal compressive strength) in Class I mortar: one brick wall (230mm) | m2 | 14
|  | Brickwork of NFP bricks in Class II mortar: one brick wall (230mm) | m2 | 34.1
|  | Brickforce, 150mm wide x 2.8mm x 20m roll | per 20 m roll | 13
|  | 2 layers: 3-ply malthoid for wall joint: 225mm wide x 20m roll | m | 20
|  | 0.58mm thk steel plate for wall joint (to soffit of roof): per m2 | m2 | 4.5
|  | Readymix - Grade 30/19 - Footings | m3 | 3.1
|  | Readymix - Grade 30/19 - Floor slab & apron | m3 | 3.7
|  | Readymix - Grade 30/19 - Roof slab | m3 | 4.4
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B10: BUILDING WORK: REFURB, RE-BUILD AND NEW (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
|  | High tensile steel bar reinforcement (all diameters): supply, cut, bend and install | t | 0.93
|  | Finishing top surfaces of concrete smooth with a wood float: (max tolerance of 3mm) | m2 | 26
|  | Finishing top surfaces of concrete smooth with a steel float: | m2 | 43
|  | Smooth Formwork (Degree of accuracy I): To walls / vertical faces | m2 | 4
|  | Smooth Formwork (Degree of accuracy I): To roof or slab soffit: slabs propped up exceeding 1,5m and not exceeding 3,5m high | m2 | 18.5
|  | Rough Formwork (Degree of accuracy II): To base | m2 | 2
|  | Making and testing 150 x 150 x 150mm concrete strength test cube | no | 6
Chlorination building (exist)
|  | Security Door: Heavy duty swing type: 2m high x 0.785m wide | no | 1
|  | Heavy duty, high security, special swing type door to accommodate hoist beam: size: 2.4m x 2m with I-Beam opening, locking bar and lock | no | 1
|  | Refurb ex bldg interior: painting | sum | 1
Building works ( not captured elsewhere)
|  | Steel droor & frame complete (Robmeg or similar): 890 x 2000mm | no | 1
|  | 'Trox'' or equal and approved door type STS complete. Door size 900 x 2100mm high | no | 1
|  | Security Door: Heavy dudty, 2m high x 0.785m wide | no | 1
|  | Meranti wood door: 890mm x 2000mm high | no | 1
|  | Door frame: Steel: 900mm x 2100mm | no | 1
|  | Aluminium window complete incl. frame and glass): Window sizes exceeding 0.5m² not exceeding 1m² | no | 3
|  | Aluminium window complete incl. frame and glass): Window sizes exceeding 1m² not exceeding 1.5m² | no | 2
|  | Burglar Bars to 5 no of windows: Guard house building. 20mm square bars, welded and epoxy coated. M8 x 40mm fasteners included | sum | 1
|  | Gypsy Vandal Resistant or equivalent low level 90 degree outlet washdown pan with vandal proof cistern, complete with heavy duty double flap toilet seat | no | 1
|  | 510 x 400mm, 'Daisy' or equivalent white vitreous china lavatory basin (code 7008) with one taphole, including integrated overflow and chainstay, bolted to wall | no | 1
|  | Internal pipework for wash basin & toilet - all inclusive sum | sum | 1
|  | Furniture: Varnished Pine counter | sum | 1
|  | Furniture: Office Chair | sum | 1
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B10: BUILDING WORK: REFURB, RE-BUILD AND NEW (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Existing Staff Building nr MCC Plant Room
|  | Refurbish: new RC roof, windows, doors, services | sum | 1
|  | Certificate of Compliance for plumbing & drainage installation for Office Building | no | 1
Transformer Sub-Station Area
|  | Trench Excavations - Foundations: 0.8m deep | m3 | 0
|  | Open face excavation: Floor slab | m3 | 21.321
|  | Rip and compact in-situ (0.15m thk) to 93% MOD AASHTO | m3 | 5.85
|  | G7: Under floors, steps, pavings, etc. Roadworks. Compact to 93% / 100% (for SAND) MOD AASHTO: 0.15m thk | m3 | 5.85
|  | G5: Under floors, steps, pavings, etc. Compact to 98% MOD AASHTO: 0.3m thk | m3 | 11.7
Diesel Generator, Civils
|  | Open face excavation | m3 | 19.6
|  | G5: Under floors, steps, pavings, etc. Compact to 98% MOD AASHTO | m3 | 5.88
Diesel Generator, Civils
RC structure (buried bund) with G7 sandfill (compacted to 93% MOD AASHTO) and removable concrete cover panels. Excludes cost of 5000 L diesel tank (included with Elect Eng's BOQ). See items below:
|  | Exceeding 2m and not exceeding 4m deep | m3 | 70
|  | G7: Under floors, steps, pavings, etc. Roadworks. Compact to 93% / 100% (for SAND) MOD AASHTO | m3 | 10
|  | Backfilling from on-site / stockpile to trenches, holes, etc. Compact to 98% MOD AASHTO unless otherwise indicated | m3 | 45.0523
|  | Spoil incl. 5km freehaul; Intermediate excavation | m3 | 24.9477
|  | Miscellaneous - Inspection lid and finishing works | Prov sum | 1 | 18000 | 18000
Total Carried Forward To Summary

## Sche B11_0
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE B11: STEEL & METAL WORK (RAILINGS, VALVES, MISCELLANEOUS) | SCHEDULE B10: STEEL & METAL WORK (RAILINGS, VALVES, MISCELLANEOUS) | SCHEDULE B10: STEEL & METAL WORK (RAILINGS, VALVES, MISCELLANEOUS) | SCHEDULE B10: STEEL & METAL WORK (RAILINGS, VALVES, MISCELLANEOUS)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B11 |  | SCHEDULE B11: STEEL & METAL WORK (RAILINGS, VALVES, MISCELLANEOUS)
Handstops
|  | Aluminium Handstop + frame: 200 wide x 500mm high (Imhoff Tank), Gereg Sewage & Water Equipment o.s.a. | no | 2
|  | Aluminium Handstop + frame: 1000 wide x 545mm high (Inlet chamber to Bio-filter), Gereg Sewage & Water Equipment o.s.a. | no | 2
|  | Aluminium Handstop + frame: 300 wide x 1000mm high (Inlet works, maint channel), Gereg Sewage & Water Equipment o.s.a. | no | 1
|  | Aluminium Handstop + frame: 800 wide x 1000mm high (Inlet works, downstr end of ex grit channel), Gereg Sewage & Water Equipment o.s.a. | no | 2
|  | Galvanised chain (1m length) and wall mounted GMS bracket for securing handstop | no | 7
Sluice Valves: Refurbish
|  | Ex penstock valves not replaced; grease moving parts and paint all CI metal work with red oxy primer and topcoat | no | 6
Remove and replace components:
|  | Remove valve cap & replace: DN450 square sluice valve | no | 3
|  | Remove valve cap & replace: DN600 square sluice valve | no | 3
Wall mounted sluice gate valve: Test, if faulty and in poor condition, then remove and replace existing in whole
|  | Test and inspect exusting sluice valve and grease all moving parts | no | 4
Wall mounted sluice gate valve: Test, if faulty and in poor condition, then remove and replace existing in whole
|  | Test and inspect exusting sluice valve and grease all moving parts | no | 4
Replace wall mounted sluice gate complete
|  | Remove existing wall mounted sluice gate and frame (complete unit): DN300 pipe opening. Manhole up to 2m deep | no | 1
|  | Remove existing wall mounted sluice gate and frame (complete unit): DN450 pipe opening. Manhole up to 3m deep | no | 2
|  | Remove existing wall mounted sluice gate and frame (complete unit): DN600 pipe opening. Manhole up to 4m deep | no | 1
|  | Wall Mounted Sluice Gate: For manhole depth up to 3m. Size: DN300 pipe opening, on-seat pressure. Complete unit incl. frame, brackets, seals, flush invert, T-key cap. Gereg or similar approved | no | 2
|  | Wall Mounted Sluice Gate: For manhole depth up to 3m. Size: DN450 pipe opening, on-seat pressure. Complete unit incl. frame, brackets, seals, flush invert, T-key cap. Gereg or similar approved | no | 2
|  | Wall Mounted Sluice Gate: For manhole depth up to 4.15m. Size: DN600 pipe opening, on-seat pressure. Complete unit incl. frame, brackets, seals, flush invert, T-key cap. Gereg or similar approved | no | 1
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B11: STEEL & METAL WORK (RAILINGS, VALVES, MISCELLANEOUS) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Channel Sluice Gates (New)
Install Channel Sluice Gate (manual screw type, type G, frame imbedded in floor. Pickled & Passivated SS 304L. Complete with handwheel and neoprene seals. For the following sizes:
|  | 300 mm wide x 1000 mm deep (for maint channel) | no | 0
|  | 700 mm wide x 1000 mm deep (for inlet works channels) | no | 2
|  | 801 mm wide x 1000 mm deep (for upstream end of grit channels) | no | 2
Handrails
GMS Handrails: All inclusive rate for supply, delivery and installation. Horizontal galvanised ball type balustrades 1000mm high, 2 Rail system consisting of continous 34mm external diameter x 2.4mm thick handrails with 43mm external diameter x 2.5mm thick uprights stanchions welded to 100mm diameter circular base plates bolted to concrete / steel with M12 stainless steel bolts (80mm long chemset bolts for concrete fastening)
|  | GMS Handrailings (Flow Control chamber to BNRAS, strategic locations) | m | 5
|  | GMS Handrailings (Existing Imhoff Tank) | m | 45.2
|  | GMS Handrailings (Bio-filter access platform & walkway) | m | 6.3
|  | GMS Handrailings (BNRAS) | m | 235.3
|  | GMS Handrailings (RAS Sump) | m | 10
|  | GMS Handrailings (Replace handrailings at outlet structures & water re-use pump manhole) | m | 36
|  | GMS Handrailing (Inlet Works channel, maintenance walkways & grit channels, selected areas only) | m | 87.1
|  | GMS Handrailing (Around vortex de-gritters) | m | 15
|  | GMS Handrailing (Biofilter) | m | 7.1
Access Gratings: Walkways, Platforms & Manholes
Clarifier Access walkway: 10.785m long x 0.8m wide
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 8.628
|  | 50 x 50 x 5mm L-section frame (angle) in lengths not exceeding 13m welded to mentis grating (mentis grating measured elsewhere) including 14mm diameter holes for bolts | m | 10.785
Structural Steelwork: RAS Chamber
Grid: RAS Sump (2.5m x 2.5m)
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 6.25
|  | 50 x 50 x 5mm L-section frame (angle) in lengths not exceeding 13m welded to mentis grating (mentis grating measured elsewhere) including 14mm diameter holes for bolts | m | 20
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B11: STEEL & METAL WORK (RAILINGS, VALVES, MISCELLANEOUS) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
GMS Grids for Manholes and Chambers:
GMS Grid for manhole MH16 (1m x 2m with 0.15m x 0.15m cut-out)
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 2
GMS Grid for manhole MH4, MH22, MH23, MH24, MH25, MH26 (each: 1.5m x 1.5m with 0.15m x 0.15m cut-out)
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 13.5
GMS Grid for manhole MH13, MH18 (WAS Chamber), MH20 & MH21 (each: 1.5m x 1.5m with 0.15m x 0.15m cut-out)
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 9
GMS Grid for manhole MH15 (1m x 1.5m with 0.4m x 0.5m trap door cut-out)
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 1.5
GMS Grid for manhole MH27 (1m x 1.16m with 0.15m x 0.15m cut-out)
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 1.2
Angle frame for manholes MH13, MH18 (WAS), MH20, MH21 and MH15
|  | 50 x 50 x 5mm L-section frame in lengths not exceeding 13m welded to mentis grating (mentis grating measured elsewhere) including 14mm diameter holes for bolts | m | 36
Information Signboards
|  | Supply and erect information signoards complete on site in accordance with Engineer's specifications and in compliance with Water Use Licence Conditions. Signboards to include amongst other, signage for "POTABLE WATER" and "NON-POTABLE WATER" | PC Sum | 1 | 20000 | 20000
BNRAS:
|  | BNRAS: Steel Access & Mixer Beams / Bridges: Inspect, treat and re-paint | sum | 1
Total Carried Forward To Summary

## Sche B12_
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE B12: PONDS: SLUDGE REMOVAL & IMPROVEMENTS. EROSION PROTECTION | SCHEDULE B11: PONDS: SLUDGE REMOVAL & IMPROVEMENTS. EROSION PROTECTION | SCHEDULE B11: PONDS: SLUDGE REMOVAL & IMPROVEMENTS. EROSION PROTECTION | SCHEDULE B11: PONDS: SLUDGE REMOVAL & IMPROVEMENTS. EROSION PROTECTION
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B12 |  | SCHEDULE B12: PONDS: SLUDGE REMOVAL & IMPROVEMENTS. EROSION PROTECTION
Ponds
|  | Clear reeds, vegetation: overflow / spillway x3 | days | 5
|  | Clear by hand / by trimmer | m2 | 6156
De-water Lagoons
|  | Using ex outlet arrangements | sum | 1
|  | Temporary overland pipe and all equipment, incl. pump to drain the Lagoons | sum | 1
|  | Sludge Removal: estimated 4375 m3, Open face excavation | m3 | 4375
|  | Remove and dispose of legally within 20km freehaul | m3 | 4375
|  | Excavate 1m x 1m hole x 1m deep following sludge removal to confirm liner system for each lagoon. Repair PE liner (where found) and re-compact all layers upon completion. SANAS Lab technician / geologist to do soil profiling and Attenberg limits | no | 3
Flow Meter Improvements (Civils Only)
|  | V-notch weir, SS304 to fit 1m width; installed at existing pond no3 outlet structure | no | 1
Water re-use System for Maintenance
|  | Water re-use plastic tank: 10,000 L (Roto or similar approved. Supply and install | no | 2
|  | Abstraction Works Chamber at Lagoon no 3 existing outlet structure: Install 1.8m dia PCC manhole ring complete with openings in bottom ring | sum | 1
|  | Valve Chamber in pond no 3 embankment; complete as per drawing no (internal pipework & fittings measured in Mech Eng bill) | sum | 1
|  | Excavations for pump base slab: measured as part of inlet works (see further above in bill) | m3 | n/a
|  | Granular G5 & compacted to 95% MOD AASHTO : measuredas part of inlet works | m3 | n/a
River Outfall, Erosion Protection Works
|  | Excavate up to 1m deep in all material and spoil within freehaul outside flood plain | m3 | 10
|  | Staircase / steps: Supply & construct using Grade 30 / 19 concrete; all inclusive (incl. formwork, smooth finish & curing) | m3 | 2
|  | Wooden handrailing with concrete to posts: Treated timber structure 1.5 m high x 15m long | m | 15
|  | Supply & install new Gabion mattress and unweathered rock - complete with A2 bidim. Dimensions: 2m L x 1m H x 1m W | no | 3
|  | Grass cutting / clear overgrown vegetation | m2 | 20
|  | Compact in-situ material to 90% MOD AASHTO | m3 | 13
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE B12: PONDS: SLUDGE REMOVAL & IMPROVEMENTS. EROSION PROTECTION | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Sludge Treatment & Management
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 4.1325
|  | Type RS40 Mentis Rectagrid non-slip (30 x 4.5mm banded non-slip) or equivalent steel grating finished on all sides with flat plate ends, hot dipped galvanised welded onto steel angle framing including all necessary cutting, trimming, fixing, etc. to horizontal ceiling panels (framing elsewhere measured) | m2 | 0.8
|  | 50 x 50 x 5mm L-section frame in lengths not exceeding 13m welded to mentis grating (mentis grating measured elsewhere) including 14mm diameter holes for bolts | m | 2.4
|  | Readymix - Grade 30/19 - Footings / Floor slab | m3 | 1
|  | Readymic Concrete for walls | m3 | 1
|  | Wire brushing of concrete surfaces to expose aggregate: Walls, floors | m2 | 4
Total Carried Forward To Summary

## Sche B13
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE B13: BUILDING WORKS - SPARES | SCHEDULE B12: BUILDING WORKS - SPARES | SCHEDULE B12: BUILDING WORKS - SPARES | SCHEDULE B12: BUILDING WORKS - SPARES
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
B13 |  | SHEDULE B13: BUILDING WORKS - SPARES
|  | (a) Supply, deliver and place in storage. Civil and Building spares as per list of items identified by the Engineer and Employer following inputs by MaP Water. Items in (a) to include Contractor mark-up of 10% (mark-up only if non-standard item as quoted elsewhere in the schedules). | Prov sum | 1 | 100000 | 100000
Total Carried Forward To Summary | [5 empty] | 100000

## Sche C1
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE C1 : ELECTRICAL: BULK FEEDER, TRANSFORMER & SWITCHGEAR | SCHEDULE C1 : ELECTRICAL: BULK FEEDER, TRANSFORMER & SWITCHGEAR | SCHEDULE C1 : ELECTRICAL: BULK FEEDER, TRANSFORMER & SWITCHGEAR | SCHEDULE C1 : ELECTRICAL: BULK FEEDER, TRANSFORMER & SWITCHGEAR
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
C1 |  | SCHEDULE C1 : ELECTRICAL: BULK FEEDER, TRANSFORMER, SWITCHGEAR and PFC
Preamable To enable electrical supply to the site (previously vandalised), approximate 120 m of the MV OH line must be re-built and end of line terminated. Interaction with the local Municipality is deemed necessary to officiate works as well as covel re- connection fees. The overhead line must be slightly re-aligned to terminate inside the secure area.
C1.1 | SANS 10280, IEC 61284, SANS 1700, SANS 121 (Part 2) and SANS 935, Standard Eskom OH Stds Specification, 5.16 - PE MVOL - PS | Overhead Line Feed to works Supply materials and extend 11 kV overhead line from current tied up point in a straight line to a point about 10m from the pallisade, terminate and anchor. Construct a take off point to 10m within the enclosure and teminate with a dropout link set 25A. Standards in accordance with MAP Standard of overhead line construction. Include poles, anchors, cross ties, clamps and excavation and planting of poles
| PS | 01. Survey, mark and peg extention on route of line, position of poles and anchors. | Number | 1
| SANS 1507-2 | 02. 70 mm2 x 3 cu XLPE 11 kV cable, complete with outdoor termination kit. | Meter | 20
| SANS 780 Et al ISO 9001:2015, PS 5.14 EMSH | 03. Supply and deliver miniature substation complete, 11 to 400 Volt 400 kVA Delta - Star including plinth complete with 3 way RMU as per engineers drawing and specification | Number | 1
| IEEE Standard C62.11, IEC Standard 6099-4, PS 5.2-EELP | 04. Surge arrestors, supply and install | Number | 1 |  |  | SANS IEC 61024-1
| Eskom Code | 05. Drop out fuze set (Cut-out), supply and install | Number | 1
| Eskom Code | 06. Poles, 11 meter, supply excavate and install | Number | 3
| Eskom Code | 07. Conductor, Mink, supply and install | Meter | 510
| Eskom Code | 08. Cross arms, supply and install | Number | 7
| SABS | 09. Galvanised steel kicker pipe ND 86 mm to protect cable (fixed with SS "Band-It" straps every 500 mm agaist pole) | Meter | 10
|  | 10. Transport to deliver all OH material to site to erect | The lot | 1
| MAP | 11. Interface, registration, application, approvals with local authority to proceed with the project, test and energise. | The lot | 1
| MAP | 12. Connection and deposit/metering fees payable to the municipality | The lot | 1
| MAP | 12. Construct, co-ordinate with the Municipality/ESKOM, test, certify and commission | The lot | 1
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE C1 : ELECTRICAL: BULK FEEDER, TRANSFORMER & SWITCHGEAR | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
Primary LV Supply
Preamable
The provision of primary and secondary supply to the site entail connection of the 400 kVA transformer MV to the overhead feeder and the LV supply to the change over system. The secondary supply entail the provision and installation of a 350 kVA self-contained diesel generator with an automatic change over switch to cycle between primary and secondary supply in a safe and controlled manner.
C.1.2 |  | Primary supply, transforming
C.1.2.1 | SANS 780 Et al ISO 9001:2015, PS 5.14 EMSH, Specification 5.20 - PE EPTM | 01. Supply and deliver miniature substation complete, 11 to 400 Volt 400 kVA Delta - Star including plinth complete with 3 way RMU as per engineers drawing and specification | Number | 1
|  | 02.Supply and offload cable | Meter | 30
|  | 03. Install cable as per the engineers drawing | Meter | 30
|  | 04. Terminate, pressure test (Term kit included) | Number | 2
C.1.3 | PS | Power Factor Correction 400 Volt, 3 Phase, 50 hz, 52,5 kVAr (Achieve unity)
C1.3.1 | IEC 61439-2,IEC 60831 & IEC 61921 | This work entail the design, manufacture install and commission of a power factor correction unit in the main control room. Final position will be determined on site. A cicuit breaker must be provided by the Contractor in the main LV panel in the non essential section. The panels and components are to be type tested at a recognised and well-reputed test laboratory. Type test certificates shall be available for verification as evidence of successful completion of type tests. It is the manufacturer and supplier’s responsibility to submit all type test reports for the PFC equipment offered.
|  | 01. Supply, deliver to site and install | Lot | 1
|  | 02. Installation and termination to LV panel (NES) section | Lot
|  | 03. Cold commissioning | Lot
| IEC 61439-2. | 04. Commission, test, certification and issue compliance report | Lot
Total Carried Forward To Summary

## Sche C2
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE C2 : ELECTRICAL: LV CABLES (RETIC) | SCHEDULE C2 : ELECTRICAL: LV CABLES (RETIC) | SCHEDULE C2 : ELECTRICAL: LV CABLES (RETIC) | SCHEDULE C2 : ELECTRICAL: LV CABLES (RETIC)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
C2 |  | SCHEDULE C2: ELECTRICAL : LV CABLES (RETIC)
Preamble Electrical distribution within the treatments works entail excavation cable routes, installing laying and cables and provision of manholes and a concrete protection system. (Co-ordinate with civil works). Cables will be terminated to designated pumps, actuators, sensors as well as drives, starters within power enclosures. Power distribution is split downstream for essential as well as non essential feeders and bus systems. A matching "onload isolator" complete with emergency stop, isolator with lockout facility will be installed conveniently next to all AC powered rotational machines, on an approved pedestal as per illustrative [TBA] typical layout.
C2.1 | SABS 0198-13:2016: Cable and Cable Testing, 5.4-PE EOH - PS | Main 400 Volt Distribution Cables Motor Supplies Termination and testing of the cable is deemed to include correct duty/size lugs, stainless steel bolts, nuts/washers, glands as well as correct termination and jointing kits of the cable earth continuity conductor (ECC) to the enclosure earths. All bolts shall be torqued in accordance with specification and logged in the hand over report to approval of the engineer.
C2.1.1 | Refer to C.2.1 | Main Minisub LV Busbar to Main LV Panels
|  | 01. Supply PVC SWA ECC 240 mm2 4 core Cu XLPE cable, Minisub to MLVP NE | Meter | 20
|  | 02. Install and terminate #.01 | Number | 20
|  | 03. Supply PVC SWA ECC 185 mm2 4 core Cu XLPE cable, Generator to MVLP NE | Meter | 30
|  | 04. Install and terminate #.03 | Number | 30
|  | 05. Supply PVC SWA ECC 185 mm2 4 core Cu XLPE cable, MLVP NE to MCC NE | Meter | 30
|  | 06. Install and terminate #.05 | Meter | 30
|  | 07. Supply PVC SWA ECC 185 mm2 4 core Cu XLPE cable, MLVP ES to MCC ES | Meter | 30
|  | 08. Install and terminate #.07 | Number | 30
C2.1.2 | Refer to C.2.1 | MCC Main power to pump equipment
C2.1.3 | Refer to C.2.1 | MCC to surface aerators motors
|  | 01. Supply PVC SWA ECC 16 mm2 4 core Cu XLPE cable (No 1, 2, 3, 4, 5 and 6) | Meter | 300
|  | 02. Install and terminate | Number | 300
C2.1.4 | Refer to C.2.1 | MCC to mixer motors
|  | 01. Supply PVC SWA ECC 6 mm2 4 core Cu XLPE cable (No 1, 2, 3, 4, 5 and 6) | Meter | 360
|  | 03. Install and terminate | Number | 360
C2.1.5 | Refer to C.2.1 | MCC to Re-Cycle Pumps 2 x 5,5 kW
|  | 01. Supply PVC SWA ECC 10 mm2 4 core Cu XLPE cable (No 1,2) | Meter | 60
|  | 02. Install and terminate | Number | 60
C2.1.6 | Refer to C.2.1 | MCC to WAS pumps x 2 x 7,5 kW
|  | 01. Supply PVC SWA ECC 10 mm2 4 core Cu XLPE cable (No 1, 2) | Meter | 60
|  | 02. Install and terminate | Number | 60
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE C2 : ELECTRICAL: LV CABLES (RETIC) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
C2.1.7 | Refer to C.2.1 | MCC to RAS pumps x 2 x 11kW
|  | 01. Supply PVC SWA ECC 10mm2 4 core Cu XLPE cable (No 1, 2) | Meter | 60
|  | 02. Install and terminate | Number | 60
C.2.1.8 | Refer to C.2.1 | MCC to Bridge Drive x 1 x 0,37 kW
|  | 01. Supply PVC SWA ECC 4 mm2 4 core Cu XLPE cable (No 2,4 and 6) | Meter | 40
|  | 02. Install and terminate | Number | 60
C2.1.9 | Refer to C.2.1 | MCC to Wash Reuse Pump 2 x 1,1 kW
|  | 01. Supply PVC SWA ECC 6 mm2 4 core Cu (No 1, 2) | Meter | 360
|  | 02. Install and terminate | Number | 360
C2.1.10 | Refer to C.2.1 | MCC to Weir outlet actuator (1x )
|  | 01. Supply PVC SWA ECC 4 mm2 4 core Cu | Meter | 120
|  | 02. Install and terminate | Number | 120
C2.1.11 | Refer to C.2.1 | Process Control (MCC) power supply to Field Monitors and sensing equipment. Include installation of cables, jointing, terminating materials, all earth wires and cable name tags as per the cables schedule
|  | 01. Supply PVC SWA ECC 2,5 mm2 4 core Cu | Meter | 750
|  | 02. Install and terminate | Number | 650
C2.2 | Refer to C.2.1 | MCC Main to downstream Sub DB's
C2.2.1 | Refer to C.2.1 | Main LV to mast flood lights 3 x 6 x 0,5 kW
|  | 01. Supply PVC SWA ECC 16 mm2 4 core Cu (no 1, 2 3) | Meter | 160
| Refer to C.2.1 | 02. Install and terminate | Meter | 160
C2.2.2 | Refer to C.2.1 | Main LV to Mast Flood Lights 4-5
|  | 03.Supply PVC SWA ECC 16 mm2 4 core Cu (No 4, 5) | Meter | 260
|  | 04. Install and terminate | Meter | 260
| Refer to C.2.1 | Main LV to Chlorination contact premises
|  | 01. Supply PVC SWA ECC 10 mm2 4 core Cu | Meter | 250
|  | 02. Install and terminate | Meter | 250
C2.2.3 | Refer to C.2.1 | Main LV to Head of Works
|  | 01. Supply PVC SWA ECC 25 mm2 4 core Cu | Meter | 310
|  | 02. Install and terminate | Number | 310
C2.3 | Refer to C.2.1 | Head of Works, Raw waste water inlet
C2.3.1 | Refer to C.2.1 | MCC to wash water pump 1x 0,37 kW
|  | 01. Supply PVC SWA ECC 4 mm2 4 core Cu (No 1) | Meter | 45
|  | 02. Install and terminate | Number | 45
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE C2 : ELECTRICAL: LV CABLES (RETIC) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
C2.3.2 | Refer to C.2.1 | MCC to mechanical screen 1x 1,1 kW
|  | 01. Supply PVC SWA ECC 4 mm2 4 core Cu (No 1) | Meter | 30
|  | 02. Install and terminate | Number | 30
C2.3.4 | Refer to C.2.1 | MCC to screen conveyor 1x 0,75 kW
|  | 01. Supply PVC SWA ECC 4 mm2 4 core Cu (No 1) | Meter | 30
|  | 02. Install and terminate | Number | 30
C2.3.5 | Refer to C.2.1 | MCC to wash compactor 1x 1,5kW
|  | 01. Supply PVC SWA ECC 4 mm2 4 core Cu (No 1) | Meter | 30
|  | 02. Install and terminate | Number | 30
C2.3.6 | Refer to C.2.1 | MCC to grid classifier motor 1x 0,55 kW
|  | 01. Supply PVC SWA ECC 4 mm2 4 core Cu (No 1) | Meter | 30
|  | 02. Install and terminate | Number | 30
C2.3.7 | Refer to C.2.1 | MCC to grid classifier pumps 2 x 5 kW
|  | 01. Supply PVC SWA ECC 4 mm2 4 core Cu (No 1, 2) | Meter | 70
|  | 02. Install and terminate | Number | 70
C2.3.8 | Refer to C.2.1 | MCC to vortex degritter stirrer 2 x 1,5 kW | Meter | 80
|  | 01. Supply PVC SWA ECC 4 mm2 4 core Cu (No 1, 2) |  | 80
|  | 02. Install and terminate | Number | 80
C.2.3.9 | Refer to C.2.1 | Process Control (MCC) Supply to Field Monitors and sensing equipment. Include installation of cables, jointing, terminating materials, all earth wires and cable name tags as per the cables schedule
|  | 01. Supply PVC SWA ECC 2,5 mm2 4 core Cu x 9 | Meter | 500
|  | 02. Install and terminate (1 to 9) | Number | 500
|  | 03. Supply and install 25 mm ID BOSAL Conduit, galvanised , 3 meter length (include .04 to .12) | Number | 30
|  | 04. BOSAL 25 mm Bends, 90 Degrs | Number | 20
|  | 05. BOSAL 25 mm Sockets (Joints) | Number | 20
|  | 06. BOSAL 25 mm Saddle Spacers | Number | 60
|  | 07. Pratley 25 mm 2 way surface termination Box | Number | 30
|  | 08. BOSAL 25 mm flat saddles | Number | 40
|  | 09. Pratley Gland and Shrouds No 0 | Number | 60
|  | 10. Pratley Gland and Shrouds No 1 | Number | 50
|  | 11. Pratley Gland and Shrouds No 2 | Number | 20
|  | 12. Pratley Gland and Shrouds No 3 | Number | 10
Total Carried Forward To Summary

## Sche C3
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE C3 : ELECTRICAL & ELECTRONIC: MCC's - INLET WORKS & MAIN PLANT ROOM | SCHEDULE C3 : ELECTRICAL & ELECTRONIC: MCC's - INLET WORKS & MAIN PLANT ROOM | SCHEDULE C3 : ELECTRICAL & ELECTRONIC: MCC's - INLET WORKS & MAIN PLANT ROOM | SCHEDULE C3 : ELECTRICAL & ELECTRONIC: MCC's - INLET WORKS & MAIN PLANT ROOM
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
C3 |  | SCHEDULE C3 : ELECTRICAL & ELECTRONIC: MCC's - INLET WORKS & MAIN PLANT ROOM
Preamable To provide main distribution enclosures and control infrastructure, the installation of a motor control centre (MCC) equipped with variable speed as well as soft start (including direct on line) units to control and rotational speed adjustment to the site (previously vandalised). All main distribution equipment is separated to allow essental as well as non-essential supply. All motors, pumps as well as actuators are provided with a emergency local stop start and lock-out facility.
C3.1 |  | Main Motor Control Centers( MCC'S) Including drive and components, as per Drawings
| SANS 1091; -0142-P1; -;60269-2; - 60439; -60529; -60947. PS 5.5 PE MCC | The MCC consist of an essential -as well as a non-essential section fed from the corresponding sections of the main LV panel. The panel must provide for motor drives specified in matching cubicles equipped with individual doors, interlocked isolator and the door face equipped with the following: (a) 3/1 phase volt meter as applicable, (b) Thermal MD 3/1 phase ammeter with resettable analogue indicator (c) Run indicator (green) (c) off (red) (d) tripped (Amber) (e) Off, manual as well as remote auto operation selector. (f) All drives are required to be with a spring loaded 3 way toggle switch to allow in manual mode jog the motor forward/reverse in attempt to dislodge any blockage. (g) For drives 11 kW and above, the drive MMI panel must be built into the door face. Suitable Extract fans must be built into the panel to evenly vent hot air generated by the drives to ensure maximum working temperature of 45 Degrees Centigrade.
|  | 01. Manufacture, assemble and supply the Main MCC ES panel sections | Number | 1
|  | 02. Manufacture, assemble and supply the Main MCC NES panel sections | Number | 1
|  | 03. Manufacture, assemble and supply the Head of works MCC ES panel | Number | 1
|  | 02. Install the panels | Number | 3
|  | 02. Cold commission, protection setting calculations, setting, test and issue certification | Number | 3
C3.2 |  | Main Low Voltage Panels
C3.2.1 |  | Manufacture,deliver and off-load the complete Main Low Voltage Panel (ES and NE sections) to the site Including:
| SANS 556, PS 5.5 PE MCC | 01. Build, assemble, wire, install circuit breakers, busbars, load and transport and install the panel at the works in accordance with Engineers drawing XXXX. The panel cosists of a non- as well as an essental section, with feeds from the primary as well as a secondary supply, An outomatic change-over switch must be provided and installed as to disconnect the primary supply on failure and connect the secondary supply to energise the essential equipment.
|  | 01. Manufacture, assemble and supply the MLVP ES sections | Number | 1
| PS | 02. Manufacture, assemble and supply the MLVP NES sections | Number | 1
| PS | 02. Install the panels | Number | 2
| PS | 02. Cold commission, test and issue certification | Number | 3
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE C3 : ELECTRICAL & ELECTRONIC: MCC's - INLET WORKS & MAIN PLANT ROOM | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
C3.2.2 | PS and C. Spec MCC , FVD, SS, DOL,, Specification 5.5 -PE - MCC | Supply Motor start drives and controllers to install, terminate and wirin cotroller circuits and wire in indicators, selectors, isolators as well as status indicators in the MC enclosures. The successful contractor must align with the Panel Builders and co-ordinate the supply the units, install, wire and test.
|  | 01. 30kW 400 Volt 3 phase units (vfd) | Number | 6
|  | 02. 11 kW 400 Volt 3 phase units (vfd) | Number | 3
|  | 03. 7,5kW 400 Volt 3 phase units (ss) | Number | 2
|  | 04. 5,5 kW 400 Volt 3 phase units (ss) | Number | 2
|  | 05. 1,5 kW 400 Volt 3 phase units (ss) | Number | 6
|  | 06. 2,0 kW 400 Volt 3 phase unit (ss) | Number | 1
|  | 07. 0,5 kW 400 Volt 3 phase unit (dol) | Number | 6
|  | 08. Manufacture and supply stop start lockout units | Number | 27
|  | 09.Install #.08 | Number | 27
|  | .10 UPS, 1500 VA for control circuits with 30 minute battery backup. To be handed to the panel builder for installation and termination. Make and model to be approved by the engineer. | Number | 3
|  | .11 Reversing contactor set for each of the above | Number | 26
|  | .12 Panel mount rotary selector switches, off, manual and remote. | Number | 26
|  | .13 Panel mount status lights, red, green, amber, and blue | Number | 120
|  | .14 Panel mount spring mounted toggle switch, 2 way | Number | 26
|  | .15 Start button, spring loaded push type, green. | Number | 26
|  | .16 Stop button, spring loaded push type, red, include emergency stop and lockout | Number | 26
|  | .17 Power supply, stabilised 24 Volt DC 500 VA for control circuits feeding of the UPS circuits. To be handed to the panel builder for installation and termination. Make and model to be approved by the engineer. | Number | 3
C.3.3 |  | Design, drawing , Installation
Rate tendered to include for all plant, tools, labour, rigging, handling, placing into position, aligning, fixing, grouting, but not limited to and getting ready for testing and commissioning Install of switchgear shall be accordance with the manufacturer's written instructions and recognized industry practices, to ensure that the switchgear complies with the requirements and serves the intended purposes. Comply with the requirements of SABS and IEC standards and applicable portions of "Standard of Installation", for installation of switchgear but not limited to.
|  | 01. Equipment required for site installation of MCC's | Sum | 1
|  | 02. Protection setting calculations and setting of protection relays | Sum | 1
Total Carried Forward To Summary

## Sche C4
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE C4 : ELECTRICAL & ELECTRONIC: CONTROL, PLC, TELEMETRY, INSTRUMENTS | SCHEDULE C4 : ELECTRICAL & ELECTRONIC: CONTROL, PLC, TELEMETRY, INSTRUMENTS | SCHEDULE C4 : ELECTRICAL & ELECTRONIC: CONTROL, PLC, TELEMETRY, INSTRUMENTS | SCHEDULE C4 : ELECTRICAL & ELECTRONIC: CONTROL, PLC, TELEMETRY, INSTRUMENTS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
C4 |  | SCHEDULE C4 : ELECTRICAL & ELECTRONIC: CONTROL, PLC, TELEMETRY, INSTRUMENTS
C4.1 |  | OTHER FIXED PRICE ITEMS THAT ARE PRICED ELSEWHERE (NOTE: THESE ITEMS ARE PRICED IN THE A-SCHEDULES AS REFERENCED BELOW)
C4.1.1 |  | Site establishment and Site clearance: Included with Pricing elsewhere under Schedule A1 (various items) | n/a |  | n/a | n/a
C4.1.2 | PEI-PLC-26.3 | Occupational and Safety requirements such OHS file, etc. Included with Pricing elsewhere under Schedule A3 (item A3.1.2.1) | n/a |  | n/a | n/a
C4.1.3 | PEI-PLC-26.3 | Allow for testing and commissioning of the whole electronic installation. Included with Pricing elsewhere under Schedule A4 (item A4.3.2.1) | n/a |  | n/a | n/a
C4.1.4 | PEI-PLC-26.3 | Training of PE-PLC System Included with Pricing elsewhere under Schedule A4 (item A4.1.4.1) | n/a |  | n/a | n/a
C4.1.10 |  | OTHER FIXED PRICE ITEMS (SCHEDULE C4)
C4.1.10.1 | PEI-PLC-26.3 | PLC Manuals and documentation as per PE-PLC 6.16 in the specifications. (Note that the Principal Contractor are to compile these PLC documentation into the O & Manual - with last mentioned priced seperately in Schedule A3) | sum | 1
C4.1.10.2 | PEI-PLC-26.3 | 12 Month Guarantee | sum | 1
C4.2 |  | ENCLOSURES & EQUIPMENT
Note that the system as per drawings 10909001-7019 to 7022 allow for 205 inputs and outputs. This include ultrasonic flow meters, clamp on flow meters, electronic current switches, temperature switch, manual-auto-off switches, push buttons, pressure switches, level indicators, limit switches, solenoid valves, run time of certain motors, timers, current, voltage, frequency. etc. The inputs and outputs will more or less divided between the 2 PLC's.
C4.2.1 | PEI-PLC-26.1 | Supply and install equipment in a 19 inch rack. See PE-PLC 6.2 in the specifications. | unit | 2
C4.2.2 | PEI-PLC-26.4 | Supply and install a UPS with Power supply, CPU, Communication Processor for communication between the 2 PLC's, monitors, etc. as per specifications. | unit | 2
C4.3 |  | CABLING
Note that the 2 positions, Inlet Works and Main Plant rooms are approximately 100m apart. Other equipment are not more than 90m from the PLC. Sleeves installed by others.
C4.3.1 | PEI-PLC-26.3 | Supply and install communication wires CAT 6 between various equipment and the PLC. | m | 3000
C4.3.2 | PEI-PLC-26.3 | Supply and install connections/terminations for the above CAT 6 as per specification-PLC 6.1 | unit | 410
C4.3.3 | PEI-PLC-26.3 | Supply and install communication wires 8 Core fibre optic cable between PLC. Inlet works and PLC Main | m | 200
C4.3.4 | PEI-PLC-26.3 | Termination for 8 core fibre optic | unit | 4
C4.4 |  | PLC's: SUPPLY, INSTALLATION & PROGRAMMING
Note that all indicators will be supplied by others. However, the operation of indicators will be by means of the PLC's. All information indicated by MCC equipment will be indicated on the PLC monitors.
C4.4.1 | PEI-PLC-26.2 | Supply, install and program the PLC's as per specifications and above indicated drawings. | sum | 2
Total Carried Forward To Summary

## Sche C5
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE C5 : ELECTRICAL: BUILDINGS - ELECTRICAL INSTALLATIONS | SCHEDULE C5 : ELECTRICAL: BUILDINGS - ELECTRICAL INSTALLATIONS | SCHEDULE C5 : ELECTRICAL: BUILDINGS - ELECTRICAL INSTALLATIONS | SCHEDULE C5 : ELECTRICAL: BUILDINGS - ELECTRICAL INSTALLATIONS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
C5 |  | SCHEDULE C5 : ELECTRICAL: BUILDINGS - ELECTRICAL INSTALLATIONS (Power/Light) in the Main Control Room, Head of Works/Canopy,Security Control, Ablutions, Stores and river discharge channel
| Refer to PS-5.12-ESPL | Preamable: This work entail construction/installation of the internal power, lights, wiring, socket outlets, light switches and distribution enclosure as per specification [TBA], The successfu l contracter will utilise surface mount components but wiring to be recessed by means of chasing and plastered over. The luminaires are specified in PS Table A.
Light Fittings
| Type A | Indoor vandal guard suface mount Class 1 230 Volt, 50 Hz, 18 Watt LED bulkhead fitting (vertical). Complete with die cast aluminium body, high impact resistant policarbonate (frosted) diffuser.The general shape would prevent positive grip on the housing. In addition, the following: (1) Tamper proof Stainless Steel screws and special tool. (2) Single piece silicone gaskit (3) Efficacy of not less than 95 Lumen/Watt (4) IP 65 (5) Power factor > 0,95 (6) bottom entry cable (7) SVM > 0,4 (8) THD < 12 % (9) 120 deg spread. (10) 4000 K color. |  |  |  | n/a
| Type B | Indoor vandal guard suface mount liniar type Class 1 230 Volt, 50 Hz, 58 Watt LED bulkhead fitting (vertical). Complete with die cast aluminium body in white finish, high impact resistant policarbonate (frosted) diffuser.The general shape would prevent positive grip on the housing. In addition, the following: (1) Tamper proof Stainless Steel screws and special tool. (2) Single piece silicone gaskit (3) Efficacy of not less than 95 Lumen/Watt (4) IP 66 (5) Power factor > 0,95 (6) bottom entry cable (7) SVM > 0,4 (8) THD < 12 % (9) 120 deg spread. (10) 4000 K, stainless steel clips. |  |  |  | n/a
| Type C | Post top mount bottom entry type Class 1 230 Volt, 50 Hz, 80 Watt LED streetlight fitting (horisontal adjustable tilt). Complete with die cast aluminium body in silver PC finish, high impact resistant glass lens with protector. The general shape would prevent positive grip on the housing. In addition, the following: (1) Tamper proof Stainless Steel screws and special tool. (2) Single piece silicone gaskit (3) Efficacy of not less than 95 Lumen/Watt (4) IP 65 (5) Power factor > 0,95 (6) bottom entry cable (7) SVM > 0,4 (8) THD < 12 % (9) 120 deg spread. (10) 4000 K, stainless steel fixings and screws. |  |  |  | n/a
| Type D | Mast top mount type Class 1 230 Volt, 50 Hz, 500 Watt LED floodlight fitting (adjustable tilt). Complete with die cast ADC12 aluminium body in silver PC finish, high impact resistant polycarbonate lens with protector. In addition, the following: (1) Tamper proof Stainless Steel screws and special tool. (2) Single piece silicone gaskit (3) Efficacy of not less than 180 Lumen/Watt (4) IP 65 (5) Power factor > 0,97 (6) bottom/side entry cable (7) SVM > 0,4 (8) THD < 15 % (9) Adjustable spread. (10) 4000 K, stainless steel fixings and screws. (11) SMD 3030 LED |  |  |  | n/a
C5.1 |  | Premises DB enclosures
C5.1.1 | SANS 1619, SANS 156 | 01.Supply and deliver surface mount Sub DB Enclosures for the premises as per specification and engineers approval. These enclosures must be completly wired and fitted with main 2 pole isolator, 60 Amp earth leakage, 2 x 20 A plug circuits as well as 2 x 10 Amp light circuits, complete with earth and neutral bar. Fault level rated at 10 kA. | Number | 5
C5.1.2 |  | 02. Install DB's, terminate to circuitt wiring include small building works required to make chasing and plaster good. | Number | 5
C5.2 | PS 5.12-ESPL | Internal Illumination
C5.2.1 | SANS 475 and 10114-1. Refer to Light fitting schedule | 01.Supply, deliver internal bulkhead fittings (Type A) for the various premises as per specification, and engineers approval. | Number | 15
C5.2.2 |  | 01.Supply, deliver internal bulkhead fittings (Type B) for the various premises as per specification and engineers approval. | Number | 5
C5.2.3 |  | 03. Install light fittings, terminate to circiut wiring as well as small building works required to make chasing and plaster good. | Number | 20
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE C5 : ELECTRICAL: BUILDINGS - ELECTRICAL INSTALLATIONS | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
C5.3 | PS 5.12-ESPL | Electrical socket outlets, single and 3 phase.
C5.3.1 | SANS 1239 | 01. Supply and deliver to site surface mount 15 A SSO, complete with box, coverplate and fixings | Number | 12
|  | 02. Install Socket outlet with cover plates, terminate to circiut wiring as well as small building works required to make chasing and plaster good. | Number | 12
C5.3.2 | SANS 60309-1 | 02. Supply and deliver to site 30A 3 5 Pin phase Welding Outlet and male socket complete with internal isolator/interlock | Number | 2
C5.3.3 |  | 03. Install 30 Amp socket outlets complete with cover plates, terminate to circiut wiring as well as include small building works required to make chasing and plaster good. | Number | 2
C5.4.4 |  | 04. Supply Surfix/Norse type 3 core 2,5 mm2 wiring system for premises small power distribution | Meter | 200
C5.4 | PS 5.12-ESPL | Internal and external Illumination
C5.4.1 | BS 3676 | 01. Supply and deliver to site surface mount single lever light Switch complete with box/cover rated 5Amp as per Specification | Number | 10
C5.4.2 |  | 02. Install light switches (single) in works premises | Number | 10
C5.4.3 |  | 04. Chase, wire, plaster over and connect (cumulative) | Meter | 100
C5.4.4 |  | 05. Chase, wire, plaster over and connect 15 Amp socket in inlet works premises | Meter | 200
C5.6 | SANS 151 | Horisontal mounted electric water heater,100 litre reservior, steel outer casing with thermo fused porcelain enamelled cylinder. Heat loss typically less than 80 Watt per hour, with 2 kW electrical element and thermostat
C5.6.1 |  | 01.Supply and deliver 100l x 2kW fixed stoarage electrical water heater (SABS 400 kPa approved) | Number | 1
C5.6.2 | IEC 60947-3 | 01.Supply and deliver 30 Amp double pole surface mount isolator, complete with Surface mounted box and cover plate. Alternate a self contained unit can be offered. | Number | 1
C5.6.3 | SANS 10254 | 02. Install and terminate the water heater including the surface mounted double pole isolater. | Number | 1
C5.7 |  | Provisional sums stated by the Employer's Electrical Engineer:
C5.7.1 |  | 01. Supply, install and test: All LV electrical works necessary (including but not limited to wiring, conduits, fittings, selector switch for manual-auto-off function and integration into local DB) for functioning of HVAC system (see mechanical price schedule) in main MCC Plant Room. | Prov sum | 1
Total Carried Forward To Summary

## Sche C6
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE C6 : ELECTRICAL: SITE ILLUMINATION | SCHEDULE C6 : ELECTRICAL: SITE ILLUMINATION | SCHEDULE C6 : ELECTRICAL: SITE ILLUMINATION | SCHEDULE C6 : ELECTRICAL: SITE ILLUMINATION
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
SCHEDULE C6 : ELECTRICAL: SITE ILLUMINATION
C6.1 |  | Area Illumination
| Specification 5.12 - PE - SPL | Preamable To provide compliant area lighting to the treatment works, 20 meter scissor type mast as well as 6 x 400 Watt LED flood lights will be strategically installed to provide 50 Lux in accordance with Environmental Regulations. Power supply is connected to essential supply with lightning protection and bonded to earth. Prospective Contractors must note that the design and casting of a concrete suitable plinth with sleeves for 2 x16 MM2 4 core cable is included. A certificate and design approval by a Registred Structural Engineer is required. Soil conditions is available elswhere in the tendercocument however test pits is recommended for actual data.
C6.1.1 | SANS 10225 | 20 meter Midhinge type Mast Flood Lights
| All mild steel materials unless otherwise specified are grade GW355J HT Steel. Manufacturing is to SANS 10214-1987-1. All poles, masts and brackets are galvanized to ISO 1461/SANS 121-2000-1. Welding procedures to SANS 10044 parts 1-4. SP 1.12 PE ESPL | 01. Manufacture, transport, off-load masts at the site as per the specification. Include control enclosure, cable termination plate, earth studs, access door and failsafe locking device. Anchor bolts per ASTM A576. | Number | 5
|  | 02. Survey, layout and set out of positions to erect the 20 meter mast as per the Engineer's layout, obtain an excavation permit from the municipality to aid in safe excavation. | Number | 5
|  | 04. Rig, wire and mount masts on plinths and level mast, torque hold down bolts to OEM specification. | Number | 5
| SANS 60598-2-5, SANS 62262 | 05. Supply, deliver and offload at the site 500 Watt LED type flood lights (Type D), complete with clamp, stirrip and fixings | Number | 30
|  | 06. Step the mast, install and connect/terminate the flood light luminaires. This include calibration, test and aiming of the luminaires. | Number | 5
|  | 07. Manufacture and deliver a suitable electrical distribution enclosure with contactor set to distribute power and switchind from the feeder to the mast top. Control must include a fail safe daylight switch mounted at least at height of 4 meter above NGL as well as a hard wired bypass switch. | Number | 5
| SABS-03-1985, SANS 10313; -61312; 62305; -10292; -10199; - NRS076; -10142 | 01. Design, deliver and connect a suitable lightning protection system for the mast lights including a arrestor spike at the top and bond to suitable earth spikes. Include soil resistivity survey, mats/spikes, bonding, copper conductors (70 mm2 minimum). Bonding should be of the thermo type. Tie in to earth system by others. | Number | 5
| SABS XXXX | 09. Do an illumination survey within the operational area to compare design levels with actual levels achevement. Refer to SABS, incorporate and submit in compliance report | Number | 1
C6.1.2 | SANS 10225 | Post Top Streets Lights, 9 meter
| Poles are designed in accordance with SANS 10225. All mild steel materials unless otherwise specified are grade GW355J HT Steel. Manufacturing is to SANS 10214-1987-1. All poles, masts and brackets are galvanized to ISO 1461/SANS 121-2000-1. Welding procedures to SANS 10044 parts 1-4. | .01Supply and deliver street light post top steel p.ole, 9 meter, including 76 mm ID spiggot, service door, footplate included as well as cable entry cutout. A suitable cable termination glandplate (3 Way) must be provided standard with the pole. (Type C) | Number | 4
| SANS 60598-2-5, SANS 62262 | .03 Supply and deliver LED post top light luminaires, 80 Watt bottom entry suitable for 76 mm ID spiggot | Number | 4
|  | .04 Install, terminate and aim luminaire. | Number | 4
| OH&Sact | Add Equipment required, cranage, slings and safety equirment and management | Lot | 1
Total Carried Forward To Summary

## Sche C7
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE C7 : ELECTRICAL: STANDBY GENERATOR & ACCESSORIES | SCHEDULE C7 : ELECTRICAL: STANDBY GENERATOR & ACCESSORIES | SCHEDULE C7 : ELECTRICAL: STANDBY GENERATOR & ACCESSORIES | SCHEDULE C7 : ELECTRICAL: STANDBY GENERATOR & ACCESSORIES
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
C7 |  | SCHEDULE C7 : ELECTRICAL : STANDBY GENERATOR AND ACCESSORIES
C7.1 |  | Secondary power supply, self contained
| Specification 5.10 -PE- SGS PS | 01. Supply, deliver and offload a 300 kVA 3 phase 400 Volt diesel powered generator ( 10 Tonne) as per specification. | Number | 1
|  | 02. Install the generator on a plinth (provided by others) | Number | 1
C7.2 | SANS 10089-3, SANS 1535, UL 58 | Diesel fuel storage tank 4500L (Underground, composite bonded double skinned, minimum 6 mm shell thickness)
| Steel in composite, SABS 1531 Grade 355JR: | 02. Supply and deliver 4500 litre tank, with: | Number | 1
|  | 03. Matching forecourt manhole and cover | Number | 1
|  | 04. Eco safe tank sump with segmented rings | Number | 1
|  | 05. Wet leak detector, complete with bracket | Number | 1
|  | 06. Matching suction pipe complete with fittings | Number | 1
|  | 07. Screw dip pipe complete with dipstick | Number | 1
|  | 08. Ventilation stub | Number | 1
| SANS 1042 | 09. Power supply from the generator panel to the diesel tank fuel pump, incuding level control in the day tank. With 30 m 3 core (L,N and E) with glands. (no 1) | Number | 1
|  | 010. Positive suction cast iron diesel pump U/G to Day Tank Panther 56 220 Volt AC PUISI 90 Litre / Min continious duty, complete with 20 m of suitable piping. | Number | 1
|  | 11. Transportation and cranage cost | Number | 1
C.7.3 |  | Installation and commissioning of stanby plant
|  | 01. Installation of complete standby generator set as specified | Item | 1
|  | 02. Supply of complete automatic mains failure Start-up system as specified. This entail supply and delivering to the selected panel builder for installation into the MLVP NE | Item | 1
|  | 03. Installation of complete sound attenuation enclosure as specified | Item | 1
|  | 04. Installation of complete fuel tank complete with mounting frame | Item | 1
|  | Commissiong of the complete standby system | Item | 1
Total Carried Forward To Summary

## Sche C8
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE C8 : ELECTRICAL: SECURITY SYSTEMS & REGS COMPLIANCE | SCHEDULE C8 : ELECTRICAL: SECURITY SYSTEMS & REGS COMPLIANCE | SCHEDULE C8 : ELECTRICAL: SECURITY SYSTEMS & REGS COMPLIANCE | SCHEDULE C8 : ELECTRICAL: SECURITY SYSTEMS & REGS COMPLIANCE
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
C8 |  | Electrical : Security Systems and Compliance
C8.1 | PS 5.1PE SPL | Smart wireless zonal ingress/movement monitor, smoke alarm with remote activation for response.
| C8.1.1 | 01. Main control panel complete with recorder, supply. (Inclusive .02 to .16) | Number | 1
|  | 02. Remote controllers, tie in with main controller, supply. | Number | 2
|  | 03. GSM communication module and antennea, supply . | Number | 3
|  | 04. Power supply module, 8 hour standby, supply. | Number | 1
|  | 05. Man machine interface, supply. | Number | 1
|  | 06. Passive indoor infrared detectors, supply. | Number | 4
|  | 07.Smoke detector, fire/combustion products, supply. | Number | 4
|  | 08. Door/window limit/magnetic switches, supply. | Number | 10
|  | 09. CCTV dome type indoor picture capture camara/ normal and infrared, supply. | Number | 4
|  | 10. GSM or equivalent communication module to control room, include local transmitter and reciever upstream control. | Number | 1
|  | .11 Heavy duty limit switch (Magnetic) on main gate |  | 2
|  | .12 Panic button, installed in a convenient place, next to door handle, supply | Number | 5
|  | .13 Set of 4 button remote controllers, supply | Number | 4
|  | .14 Key switches (4 special cut keys keyed alike), supply | Number | 2
|  | .15 Bosal conduit, 20 mm | Lengths | 20
|  | .16 Install and test system | Complete | 1
| C8.1.1 | .01 Remote monitoring option (Refer to PS 21) | Number | 12
C8.2 |  | Electric Fence
C8.2.1 | 'OHSAct GMR, EMR #12, 13 and 14 incl Section 44, SANS60335-2-76 | Consist of installation , test and certification of a post top 5 electrified strand perimeter fence ingress deterrent and activation alarm, for post top application on existing concrete pallisade fence, 650m. There are 5 gates to traverse, one being controlled. Sleeves under the roadway and to controllers to be provided by others. | Note: The successful Contractor must submit insulator post mounting detail to the client representative for approval. The material shall be 318 stainless plate at least 3 mm in thickness. Minimum of M8 Stainless foxing bolts and nylock nuts shall be usedConcrete anchors shal be of the anodised type. This include for concrete pallisade, welded mesh and sliding gate tops. Refer to Typical Security Fence detail Drawing number 10909001-0591
|  | 01. Main control panel complete with recorder, supply, install and terminate, supply. (Inclusive of .02 to .09) | Number | 1
|  | 02. Remote controllers, tie in with main controller, supply. | Number | 2
|  | 03. GSM communication module and antennea, supply and install, supply. | Number | 3
|  | 04. Insulator posts, complete with 5 insulators /lines, supply. | Number | 700
|  | 05. Wire, twisted pair stainless steel guage, supply.. | Distance | 3000
|  | 06. Insulater leads, HT and connectors | Distance | 300
|  | 08. Clamps, springs, fixings | Number | 10
|  | .09 Install, commission and test the complete system | Complete | 1
| 'OHSA EMR | 10. Issue Electrified Fence System Compliance by Registred Person. (Include Registration Certificate in submission) | Number | 1
Total Carried Forward To Summary

## Sche C9
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE C9 : ELECTRICAL: EARTHING & LIGHTNING PROTECTION SYSTEM | SCHEDULE C9 : ELECTRICAL: EARTHING & LIGHTNING PROTECTION SYSTEM | SCHEDULE C9 : ELECTRICAL: EARTHING & LIGHTNING PROTECTION SYSTEM | SCHEDULE C9 : ELECTRICAL: EARTHING & LIGHTNING PROTECTION SYSTEM
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
C9 | SABS | SCHEDULE C9: EARTHING AND LIGHTNING PROTECTION SYSTEM
Design, Supply, Delivery, Installation, testing and commissioning of site electrical earthing system
C9.1 | SANS IEC TS 61312-2 | Provisional Sum allowed for professional survey, design, installation and test of the earthing system (Include tie in with 5 x 20 m floodlight masts in accordance with SANS and appliccable Standards. Rate tendered to include for all plant, tools, labour, rigging, handling, placing into position, aligning, fixing, grouting, but not limited to and getting ready for testing and commissioning in the following buildings (i) Main MCC Primary MV and LV distribution and transformer, Secondary power supply, Inlet works, Chlorine dosing and ablutions/offices.
| SANS 10198-12,SANS 10199, SANS 10292, SANS 10313,Specification PS 5.2 - PE ELP, | Install of earthing and lightning protection system shall be accordance with the manufacturer's written instructions and recognized industry practices, to ensure that the earthing and lightning protection system complies with the requirements and serves the intended purposes. Comply with the requirements of SABS and IEC standards and applicable portions of "Standard of Installation", for installation of earthing and lightning protection system but not limited to. |  |  |  | n/a
|  | 01. Site installation of lightning protection system complete as specified, engineer to approve. | Item | 1
|  | 02. Site installation of suitable earth-termination system (system earth mat) and earth mat as specified | Item | 1
|  | 04. Site installation of all connection points, terminals, interconnections, bonding points and test joints for the entire system including for “natural” components; | Item | 1
|  | 05. Earthing resistance survey upon completion of the excavations and test report | Item | 1
Total Carried Forward To Summary

## Sche C10
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: SCM/BID33/2025/2026
|  |  | SCHEDULE C10 : ELECTRICAL & ELECTRONIC: SPARES | SCHEDULE C10 : ELECTRICAL & ELECTRONIC: SPARES | SCHEDULE C10 : ELECTRICAL & ELECTRONIC: SPARES | SCHEDULE C10 : ELECTRICAL & ELECTRONIC: SPARES
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
C10 |  | SCHEDULE C10 : ELECTRICAL & ELECTRONIC: SPARES
Preamable
C10.1 |  | Supply, delivery and place in storage on site of critical electrical spares as well as maintenanace materials- and accessories. Components as per OEM recommendation or per Project Specification.
C10.1.1 | Refer to OEM recommendation/PS | Equipment spares, various
C10.1.1.1 |  | 01. VSD 30 kW - complete with MMI | Number | 1
|  | 02. SS 5,5 kW - complete with MMI | Number | 1
|  | 03. FO 128 Electrical cleaner, 20 Litre steel container | Litre | 25
|  | 04. VSD 11 kW - complete with MMI | Number | 1
|  | 05. Silika gel activated, sealed container | Kg | 10
06. Diesel Generator: fan-belts, switches, filters - oil/air, isolaters, oil, Radiator additive etc. This must be in line with manufacture's specification
| Engine OEM | .07 Supply filter, engine oil | Number | 5
|  | .08 Supply filter, air | Number | 10
|  | .09 Supply filters, diesel | Number | 10
|  | .10 Supply fan belt | Number | 5
|  | .11 Supply radiator additive | Litre | 30
|  | .12 Supply engine oil, diesel | Litre | 50
C10.1.2 |  | Mast flood light fitting, LED
|  | 01. 400 Watt Floodlight LED, Type D | Number | 3
Street light
|  | .01 120 Watt LED post top fitting | Number | 1
C10.1.3 |  | Overhead line equipment
|  | .01 10 Amp drop out fuse set of 3 | Number | 1
|  | .02 Link stick | Number | 1
|  | .03 5000 Volt meggar | Number | 1
|  | .04 Socket set, M8 to M30, GEDORE chrome steel | Number | 1
C10.1.3 |  | PC Sums: Spares
C10.1.3.1 |  | (a) Supply, delever and place in storage. Electrical & Electronic spares as per list of items identified by the Engineer and Employer following inputs by MaP Water. Items in (a) to include Contractor mark-up of 10% (mark-up only if non-standard item as quoted elsewhere in the schedules). | PC Sum | 1 | 40000 | 40000
Total Carried Forward To Summary

## Sche D1
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: VCW - TBC
|  |  | SCHEDULE D1 : MECHANICAL: INLET WORKS | SCHEDULE D1 : MECHANICAL: INLET WORKS | SCHEDULE D1 : MECHANICAL: INLET WORKS | SCHEDULE D1 : MECHANICAL: INLET WORKS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
D1 |  | SCHEDULE D1 : MECHANICAL: INLET WORKS
The equipment noted in the descriptions are indicated for the purpose of the description and does not intend that the particular name or company should be used. The Tenderer may offer equipment similar to those mentioned.
D1.1 |  | INLET WORKS
D1.1.1 |  | Isolate, Decommissioning and Stripping of Manual Hand Rake Screen
D1.1.2 | PEA 8.5 | Hand rake 700 mm (W) x 1,000 mm (H). | No | 1
D1.2 |  | Supply and Delivery of Inlet Works Manual Hand Rake Screen Refer drawing: 10909001-6001
D1.2.1 | PEA 8.1 | Hand rake course screen at 45°, 700 mm (W) x 1,000 mm (H) with 50 mm openings, made from stainless steel flat bar, complete with drying or washing area or drip tray and rake. Refer to ID tag 12-HN01,12-HN03 on P&ID 10909001-7001. | No | 2
D1.3 |  | Installation and Testing of Inlet Works Manual Hand Rake Screen
D1.3.1 | PEA 8.2 | Hand rake course screen at 45°, 700 mm (W) x 1,000 mm (H) with 20 mm openings, made from stainless steel flat bar, complete with drying or washing area or drip tray and rake. Refer to ID tag 12-HN01,12-HN03 on P&ID 10909001-7001. | No | 2
D1.4 |  | Supply and Delivery of Inlet Automated Mechanical Screening Equipment
D1.4.1 | PEA 8.1 | Mechanical screens with outer width of 700 mm with single motor and gearbox drive, machine body and components fabricated from stainless steel grade 304. Only Pickling and Passivation finish allowed. Motor rated at 1.1 kW. Direct on line to MCC. Quality Control Plan (QCP) and databook to be completed as directed and approved by the engineer. Refer to ID tag 12-HN02 on P&ID 10909001-7001.Refer drawing: 10909001-6002 | No | 1
D1.4.2 | PEA 8.1 | Hydro conveyor, fabricated from stainless steel grade 304, only Pickling and Passivation finish allowed. Connection to wash water including solenoid valve. Quality Control Plan (QCP) and databook to be completed as directed and approved by the engineer. Refer to ID tag 12-HC01,12-SV01 on P&ID 10909001-7001.Refer drawing: 10909001-6003 | No | 1
D1.4.3 | PEA 8.1 | Screening compactor with 30° incline discharge tube including solenoid valves, and motors. Fabricated from stainless steel grade 304. Only Pickling and Passivation finish allowed.Motor rated at 1.5 kW. Direct on line to MCC. Quality Control Plan (QCP) and databook to be completed as directed and approved by the engineer. Refer to ID tag 12-DW01 on P&ID 10909001-7001.Refer drawing: 10909001-6003 | No | 1
D1.4.4 | PEA 8.1 | Skip with 3m³ capacity, made from 2 mm mild steel, finished in yellow spray paint. | No | 1
D1.4.5 | PEI 8.1 | Level Probe for High level including cabling, wiring to fieldbox Refer to ID tag 12-LE01 on P&ID 10909001-7001 | No | 2
D1.4.6 | PEI 8.1 | Level Switch for Level Probe integration to MCC | No | 1
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE D1 : MECHANICAL: INLET WORKS | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
D1.5 |  | Material Handling, Lifting, Hoist Equipment
D1.5.1 |  | Manually operated chain block for a lifting capacity of 0.5 tons in accordance with SANS 1594:2007, or similar international quality standard, complete with all lifting tackle and cable required for the safe operation of the chain block. HOL to be ±6 m. Tested according to OHS ACT 85 of 1993 clause 18 and manufacturer standards/specifications, as minimum. | No | 1
D1.5.2 |  | Manually operated beam trolley (crawl) in accordance with SANS1824/EN13157, or similar international quality standard, with geared chain drive (plain travel) and manual brake for a lifting capacity of 0.5 tons. Beam trolley (crawl) to operate on monorail run way beam, 254x146x37, I-beam profile. Chain height at approximately 1.5m or 0.5m from floor. | No | 1
D1.6 |  | Installation, Testing and Commissioning of Inlet Automated Mechanical Screening Equipment
D1.6.1 | PEA 8.2 | Mechanical screens with outer width of 700 mm with single motor and gearbox drive, machine body and components fabricated from stainless steel grade 304. Only Pickling and Passivation finish allowed. Motor rated at 1.1 kW. Direct on line to MCC. Quality Control Plan (QCP) and databook to be completed as directed and approved by the engineer. Refer to ID tag 12-HN02 on P&ID 10909001-7001. | No | 1
D1.6.2 | PEA 8.2 | Hydro conveyor, fabricated from stainless steel grade 304, only Pickling and Passivation finish allowed. Connection to wash water including solenoid valve. Quality Control Plan (QCP) and databook to be completed as directed and approved by the engineer. Refer to ID tag 12-HC01on P&ID 10909001-7001. | No | 1
D1.6.3 | PEA 8.2 | Screening washer and compactor with 30° incline discharge tube including solenoid valves, and motors. Fabricated from stainless steel grade 304. Only Pickling and Passivation finish allowed.Motor rated at 1.5 kW. Direct on line to MCC. Quality Control Plan (QCP) and databook to be completed as directed and approved by the engineer. Refer to ID tag 12-DW01on P&ID 10909001-7001. | No | 1
D1.7 |  | Material Handling, Lifting, Hoist Equipment
D1.7.1 |  | Manually operated chain block for a lifting capacity of 0.5 tons in accordance with SANS 1594:2007, or similar international quality standard, complete with all lifting tackle and cable required for the safe operation of the chain block. HOL to be ±6 m. Tested according to OHS ACT 85 of 1993 clause 18 and manufacturer standards/specifications, as minimum. Quality Control Plan (QCP) and databook to be completed as directed and approved by the engineer. | No | 1
D1.7.2 |  | Manually operated beam trolley (crawl) in accordance with SANS1824/EN13157, or similar international quality standard, with geared chain drive (plain travel) and manual brake for a lifting capacity of 0.5 tons. Beam trolley (crawl) to operate on monorail run way beam, 254x146x37, I-beam profile. Chain height at approximately 1.5m or 0.5m from floor. Quality Control Plan (QCP) and databook to be completed as directed and approved by the engineer. | No | 1
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE D1 : MECHANICAL: INLET WORKS | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
D1.8 |  | Supply and Delivery of Vortex Degritter Equipment
D1.8.1 | PEA 8.6 | Vortex Degritter Paddle Stirrer, suitable for handling of abrasive wastewater containing inorganic solids and/or long-fibred debris. Medium: Grit and Sludge Motor: 3 phase 50 Hz, IP 55 Rated power: 0,75 kW Tank Diameter: 2500mm Drive Tube ID: 260mm Paddle: Pipe arms with end plates, SS304L Start. method: Direct on Line MCC. Refer to ID tag 13-VD01,13-VD02 on P&ID 10909001-7001. | No | 2
D1.8.2 | PEB 10.1 | Self Priming Centrifugal slurry pumps with Vortex impeller, suitable for handling of abrasive wastewater containing inorganic solids and/or long-fibred debris. Medium: Grit and Sludge Motor: 3 phase 50 Hz , IP 55 Rated power: 5 kW Impeller material: Hard Iron/Cast Iron with Belzond Coating Start. method: Direct on Line MCC. Refer to ID tag 13-CP01,13-CP02 on P&ID 10909001-7001. | No | 2
D1.8.3 | PEB 10.1 | Screw type, shaftless grit classifier SS304L with motor rated at 0.55 kW. Direct online connected to MCC. Quality Control Plan (QCP) and databook to be completed as directed and approved by the engineer. Refer to ID tag 13-F01 on P&ID 10909001-7001. Refer drawing: 10909001-6004 | No | 1
D1.8.4 | PEA 8.1 | Skip with 3m³ capacity, made from 2 mm mild steel, finish in yellow spray paint. | No | 1
D1.9 |  | Installation, Testing and Commissioning of Vortex Degritter Equipment
D1.9.1 | PEA 8.6 | Vortex Degritter Paddle Stirrer, suitable for handling of abrasive wastewater containing inorganic solids and/or long-fibred debris. Medium: Grit and Sludge Motor: 3 phase 50 Hz, IP 55 Rated power: 0,75 kW Tank Diameter: 2500mm Drive Tube ID: 260mm Paddle: Pipe arms with end plates, SS304L Start. method: Direct on Line MCC. Refer to ID tag 13-VD01,13-VD02 on P&ID 10909001-7001. | No | 2
D1.9.2 | PEB 10.2 | Self Priming Centrifugal slurry pumps with Vortex impeller, suitable for handling of abrasive wastewater containing inorganic solids and/or long-fibred debris. Medium: Grit and Sludge Motor: 3 phase 50 Hz , IP 55 Rated power: 5 kW Impeller material: Hard Iron/Cast Iron with Belzond Coating Start. method: Direct on Line MCC. Refer to ID tag 13-CP01,13-CP02 on P&ID 10909001-7001. | No | 2
D1.9.3 | PEB 10.2 | Screw type, shaftless grit classifier SS304L with motor rated at 0.55 kW. Direct online connected to MCC. Quality Control Plan (QCP) and databook to be completed as directed and approved by the engineer. Refer to ID tag 13-F01 on P&ID 10909001-7001. Refer to drawing: 10909001-6004 | No | 1
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE D1 : MECHANICAL: INLET WORKS | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
D1.10 |  | Supply , Delivery, Installation,Testing and Commissioning of Grit Pipeline to Grit Classifiers. Refer to Drawings & Pipe Schedule: 10909001-6014-01 ~ 03
D1.10.1 |  | DN 80 Stainless steel, piping including supports and fittings | m | 22
D1.10.3 |  | DN 80 Ductile Gate Valve.Stainless steel Bolts, Washers and Nuts including bolt sleeve and washer kit to prevent galvanic reaction. Refer to ID tag 13-GV02,13-GV03,13-GV05,13-GV06 on P&ID 10909001-7001. | No | 4
D1.10.4 |  | DN 80 Ball Check Valve.Stainless steel Bolts, Washers and Nuts including bolt sleeve and washer kit to prevent galvanic reaction. Refer to ID tag 13-NV01,13-NV02, on P&ID 10909001-7001. | No | 2
D1.11 |  | Supply and Delivery of Inlet Works Flow Meters
D1.11.1 | PEI 8.1 | Ultrasonic level measurement complete with sensor, converter device and transducer, data logger complete. Made in Stainless steel Includes: (a) Sensor; (b) Converter device; (c) Data logger (d) Connection to power supply (d) All required installation cables, conduit, trunking, materials, weather-proof panels, and consumables to render a complete and working installation. Refer to ID tag 15-LE01 on P&ID 10909001-7001. | No | 2
D1.12 |  | Installation, Testing and Commissioning of Inlet Works Flow Meters
D1.12.1 | PEI 8.2 | Ultrasonic level measurement complete with sensor, converter device and transducer, data logger complete. Made in Stainless steel Includes: (a) Sensor; (b) Converter device; (c) Data logger (d) Connection to power supply (d) All required installation cables, conduit, trunking, materials, weather-proof panels, and consumables to render a complete and working installation. Refer to ID tag 15-LE01 on P&ID 10909001-7001. | No | 2
D1.13 |  | Supply, Delivery, Installation, Commissioning and Testing of Washwater Pump System
D1.13.1 | PEB 10.1 PEB 10.2 | Centrifugal Washwater Pump with hydrosphere Medium: Washwater Motor: 3 Phase 50Hz, IP 55 Flow: 11l/s @ 60m Refer to ID tag 12-CP01,12-CP02, on P&ID 10909001-7001. | No | 2
D1.14 |  | Supply, Delivery, Installation and Comissioning of Pressure sensor
D1.14.1 | PEI 8.1 | Pressure Sensor including cabling, wiring to fieldbox. Refer to ID tag 12-PSH01, 12-PSL-01 on P&ID 10909001-7001. | No | 2
D1.14.2 | PEI 8.1 | Pressure Switch for Pressure Sensor integration to MCC | No | 2
D1.14.3 | PEI 8.1 | Pressure Gauge Refer to ID tag 12-PG01~03 on P&ID 10909001-7001. | No | 3
D1.15 |  | Supply, Delivery, Installation, Testing and Commissioning of Washwater Pump Pipeline and Fittings
D1.15.1 |  | DN 50 SS304, piping including supports and fittings | m | 10
D1.15.2 |  | Self Cleaning Disk Filter, automatic backwash including pressure gauges and controller. Refer to ID tag 12-MF01 on P&ID 10909001-7001. | No | 1
D1,16 |  | Supply, Delivery and Installation of Level Gauge
D1.16.1 |  | 1000mm Stainless Steel Level Staff Gauge | No | 2
Total Carried Forward To Summary

## Sche D2
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: VCW - TBC
|  |  | SCHEDULE D2 : MECHANICAL: IMHOFF TANK WORKS | SCHEDULE D2 : MECHANICAL: IMHOFF TANK WORKS | SCHEDULE D2 : MECHANICAL: IMHOFF TANK WORKS | SCHEDULE D2 : MECHANICAL: IMHOFF TANK WORKS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
D2 |  | SCHEDULE D2 : MECHANICAL: IMHOFF TANK WORKS
The equipment noted in the descriptions are indicated for the purpose of the description and does not intend that the particular name or company should be used. The Tenderer may offer equipment similar to those mentioned.
D2.1 |  | PRIMARY SETTLING IMHOFF TANK
D2.1.1 |  | Manufacture, Supply and Delivery of Primary Settling Tank Baffle Plates, SS304.Refer to drawing: 10909001-6015
D2.1.2 | PEC 7.6 | Inlet baffles and support brackets made in stainless steel as per the engineers drawing | No | 2
D2.1.3 | PEC 7.6 | Outlet weir plates and fixing washers/nuts as per the engineers drawing | No | 2
D2.1.4 |  | Hand Stops | Sum
D2.2 |  | Installation, Testing and Commissioning of Primary Settling Tank Baffle Plates.Refer to drawing: 10909001-6015
D2.2.1 | PEC 7.6 | Inlet baffles and support brackets made in stainless steel as per the engineers drawing | No | 2
D2.2.2 | PEC 7.6 | Weir Plate and support brackets made in stainless steel as per the engineers drawing | No | 2
D2.2.3 |  | Hand Stops | Sum
D2.3 |  | Isolate, Decommissioning and Stripping of Primary Settling Tank Sludge Valves
D2.3.1 |  | Ductile, DN 200, PN16, flanged gate valve, with stem cap, stem extension of ± 2,700 mm and valve handle | No | 4
D2.4 |  | Supply and Delivery of Primary Settling Tank Sludge Valves
D2.4.1 |  | Ductile iron body, DN 200, PN16, flanged gate valve, stem extension and valve handle. Refer to ID tag 16-GV01,16-GV02,16-GV03,16-GV04 on P&ID 10909001-7002. | No | 4
D2.4.2 |  | Ductile iron body, DN 200, PN16, flanged globe valve, with extended spindle to above ground level with valve hand wheel. | No | 4
D2.5 |  | Installation, Testing and Commissioning of Primary Settling Tank Sludge Valves
D2.5.1 |  | Ductile iron body, DN 200, PN16, flanged gate valve, stem extension and valve handle. Refer to ID tag 16-GV01,16-GV02,16-GV03,16-GV04 on P&ID 10909001-7002. | No | 4
D2.5.2 |  | Ductile iron body, DN 200, PN16, flanged globe valve, with extended spindle to above ground level with valve hand wheel.Refer to ID tag 16-PV01,16-PV02,16-PV03,16-PV04 on P&ID 10909001-7002. | No | 4
Total Carried Forward To Summary

## Sche D3
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: VCW - TBC
|  |  | SCHEDULE D3 : MECHANICAL: BIOFILTER WORKS | SCHEDULE D3 : MECHANICAL: BIOFILTER WORKS | SCHEDULE D3 : MECHANICAL: BIOFILTER WORKS | SCHEDULE D3 : MECHANICAL: BIOFILTER WORKS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
D3 |  | SCHEDULE D3 : MECHANICAL WORK: BIOFILTER (TRICKLING FILTER TYPE)
The equipment noted in the descriptions are indicated for the purpose of the description and does not intend that the particular name or company should be used. The Tenderer may offer equipment similar to those mentioned.
D3.1 |  | BIO FILTER.Refer to drawing: 10909001-6008-01~02
D3.1.1 |  | Isolate, Decommissioning and Stripping of Biofilter Inlet Line Drain Valve
D3.1.2 | PED 6.1 | Ductile, DN 80, PN16, flanged gate valve, with stem cap | No | 1
D3.2 |  | Supply and Delivery of Biofilter Inlet Line Drain Valve Internals
D3.2.1 | PED 6.3 | Ductile, DN 80, PN16, flanged gate valve internals, with stem cap. Refer to ID tag 25-GV01 on P&ID 10909001-7003 | No | 1
D3.3 |  | Installation, Testing and Commissioning of Biofilter Inlet Line Drain Valve
D3.3.1 | PED 6.4 | Ductile, DN 80, PN16, flanged gate valve internals, with stem cap. Refer to ID tag 25-GV01 on P&ID 10909001-7003 | No | 1
D3.4 |  | Isolate, Decommissioning and Removing of Biofilter Rotary Distribution Arm
D3.4.1 | PED 6.1 | Existing 38 m diameter Biofilter Rotary Distribution Arm | No | 1
D3.4.2 |  | Complete Refurbishment of Biofilter Rotary Distribution Arm Part
D3.4.2.1 | PED 6.1 | Existing flange mounted biofilter rotary distribution arm with top bearing on centre column, mild steel re-galvanised, 4 x ±19 m distribution arms 200 NB to 150 NB, including fasteners, cables, tie rods, new spreader plates Refer to ID tag 25-BF01 on P&ID 10909001-7003, and General Arrangement Drawing | No | 1
D3.5 |  | Installation, Testing and Commissioning of Biofilter Rotary Distribution Arm Part
D3.5.1 | PED 6.4 | Flange mounted Biofilter rotary distribution arm made from mild steel galvanised, 4 x ±19 m distribution arms 200 NB to 150 NB, including fasteners, cables, tie rods, spreader plates in stainless steel. Refer to ID tag 25-BF01 on P&ID 10909001-7003 | No | 1
D3.6 |  | Supply and Delivery of Biorector Inlet Flow Meter
D3.6.1 | PEI 8.1 | DN375-445 Clamp on Ultrasonic flow meter complete with flow sensor, converter device and transducer, data logger complete. Made in Stainless steel Includes: (a) Flow measuring sensor; (b) Converter device; (c) Data logger (d) Connection to power supply (e) All required installation cables, conduit, trunking, materials, weather-proof panels, and consumables to render a complete and working installation. Refer to ID tag 25-FE01 on P&ID 10909001-7003. | No | 1
D3.7 |  | Installation, Testing and Commissioning of Flow meter
D3.7.1 | PEI 8.2 | DN375-445 Clamp on Ultrasonic flow meter complete with flow sensor, converter device and transducer, data logger complete. Made in Stainless steel Includes: (a) Flow measuring sensor; (b) Converter device; (c) Data logger (d) Connection to power supply (e) All required installation cables, conduit, trunking, materials, weather-proof panels, and consumables to render a complete and working installation. Refer to ID tag 25-FE01 on P&ID 10909001-7003. | No | 1
Total Carried Forward To Summary

## Sche D4
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: VCW - TBC
|  |  | SCHEDULE D4 : MECHANICAL: BIOREACTOR (BNRAS) WORKS | SCHEDULE D4 : MECHANICAL: BIOREACTOR (BNRAS) WORKS | SCHEDULE D4 : MECHANICAL: BIOREACTOR (BNRAS) WORKS | SCHEDULE D4 : MECHANICAL: BIOREACTOR (BNRAS) WORKS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
D4 |  | SCHEDULE D4 : MECHANICAL WORK: BIOREACTOR FOR ACTIVATED SLUDGE
D4.1 |  | BIO REATOR
D4.1.1 |  | Isolate, Decommissioning and Stripping of Bioreactor Inlet Hand Rake Screen
D4.1.2 | PEA 8.5 | Hand rake course screen at 45°, 1,000 mm (W) x 1,000 mm (H) with 20 mm openings, made from stainless steel flat bar, complete with drying or washing area or drip tray and rake | No | 1
D4.2 |  | Supply and Delivery of Bioreactor Inlet Flow Meter
D4.2.1 | PEI 8.1 | Ultrasonic level measurement complete with sensor, converter device and transducer, data logger complete. Made in Stainless steel Includes: (a) Sensor; (b) Converter device; (c) Data logger (d) Connection to power supply (d) All required installation cables, conduit, trunking, materials, weather-proof panels, and consumables to render a complete and working installation. Refer to ID tag 22-LE01 on P&ID 10909001-7003 | No | 1
D4.3 |  | Installation, Testing and Commissioning of Bioreactor Inlet Flow Meter
D4.3.1 | PEI 8.2 | Ultrasonic level measurement complete with sensor, converter device and transducer, data logger complete. Made in Stainless steel Includes: (a) Sensor; (b) Converter device; (c) Data logger (d) Connection to power supply (d) All required installation cables, conduit, trunking, materials, weather-proof panels, and consumables to render a complete and working installation. Refer to ID tag 22-LE01 on P&ID 10909001-7003 | No | 1
D4.4 |  | Supply, Delivery and Installation of Level Gauge
D4.4.1 |  | 1000mm Stainless Steel Level Staff Gauge | No | 1
D4.5 |  | Isolate, Decommissioning and Stripping of Bioreactor Mixers
D4.5.1 | PEE 10.5 | Surface mounted top entry slow speed mixer comprising of 1.5 kW, 380V motor, gearbox, shaft and propeller. | No | 6
D4.6 |  | Design, Shop drawing, Manufacture and Delivery of Bioreactor Mixers.Refer to drawing: 10909001-6005
D4.6.1 | PEE 10.1 | Surface mounted top entry slow speed mixer comprising of 1.5 kW 400V 4P IP66 motor, Motor weather hood, Triple reduction helical gear speed reducer, Integrated gear drive and gearbox. Capable of reverse operation. Refer to ID tag 22-ZX01, 22-ZX02, 23-ZX01,23-ZX02, 23-ZX03, 23-ZX04 on P&ID 10909001-7004 | No | 6
D4.6.2 |  | Travel and accommodation and subsistence cost for the Employer/Employer's representative to witness factory acceptance testing. | PC Sum | - | - | 15000
D4.6.3 |  | Charge required by Contractor on sub-item above, for administration, attendance and profit. | % | 15000
D4.7 |  | Installation, Testing and Commissioning of Bioreactor Mixers
D4.7.1 | PEE 10.4 | Surface mounted top entry slow speed mixer comprising of 1.5 kW 400V 4P IP66 motor, Motor weather hood, Triple reduction helical gear speed reducer, Integrated gear drive and gearbox.Capable of reverse operation. Refer to ID tag 22-ZX01, 22-ZX02, 23-ZX01,23-ZX02, 23-ZX03, 23-ZX04 on P&ID 10909001-7004. | No | 6
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE D4 : MECHANICAL: BIOREACTOR (BNRAS) WORKS | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
D4.8 |  | Isolate, Decommissioning and Stripping of Bioreactor Surface Aerators
D4.8.1 | PEE 10.5 | Surface mounted top entry slow speed surface aerators comprising of 22 kW, gearbox, shaft and impeller. | No | 6
D4.9 |  | Design, Shop drawing, Manufacture and Delivery of Bioreactor Surface Aerators.Refer to drawing: 10909001-6006
D4.9.1 | PEE 10.2 | Surface mounted top entry slow speed surface aerators comprising of 30 kW 400V 4P IP66 motor, Motor weather hood, Double reduction helical gear speed reducer, Integrated gear drive and gearbox. | No | 3
D4.9.2 |  | Travel and accommodation and subsistence cost for the Employer/Employer's representative to witness factory acceptance testing. | PC sum | - | - | 15000
D4.9.3 |  | Charge required by Contractor on sub-item above, for administration, attendance and profit. | % | 15000
D4.10 |  | Refurbish, Supply and Delivery of Bioreactor Surface Aerators
D4.10.1 | PEE 10.6 | Refurbish surface aerator impellers. Refer to ID tag 24-SA01, 24-SA02, 24-SA03 on P&ID 10909001-7004. | No | 3
D4.10.2 | PEE 10.2 | Supply and delivery 30 kW 400V 4P IP66 motor, Motor weather hood, Double reduction helical gear speed reducer, Integrated gear drive and gearbox. Refer to ID tag 24-EM01, 24-EM02, 24-EM03, 24-B01, 24-B02, 24-B03 on P&ID 10909001-7004. | No | 3
D4.11 |  | Installation, Testing and Commissioning of Bioreactor Surface Aerators
D4.11.1 | PEE 10.4 | Surface mounted top entry slow speed surface aerators comprising of 30 kW 400V 4P IP66 motor, Motor weather hood, Double reduction helical gear speed reducer, Integrated gear drive and gearbox. Refer to ID tag 24-SA01, 24-SA02, 24-SA03, 24-SA04, 24-SA05, 24-SA06 on P&ID 10909001-7004. | No | 6
D4.12 |  | Isolate, Decommissioning and Stripping of Bioreactor A Recycle Pump
D4.12.1 | PEB 10.3 | Existing Axial flow propeller A recycle pumps | No | 2
D4.12.2 |  | Refurbish and Delivery of Bioreactor A-Recycle Pump
The refurbishment of the A-recycle pumps includes but not limited to: Inspection for wear, corrosion and damage particulary to the bearings (SNU513-611),flights and pulley. All worn parts should be repaired to working conditions. All damaged parts must be replaced with the same/similar parts to render a complete and working installation. Existing pulley at the top of the pump to be inspected for wear and damage with replacement or repair depending on the condition. Motor and belt connecting the pump pulley should be replaced.
D4.12.2.1 | PEB 10.4 | Axial flow propeller pumps with fixed pitch blades for high capacity low head pumping. Fluid: Screened Sewage. Rated power: 3.0kW Motor: 3 Phase, 50Hz Refer to ID tag 24-AP01, 24-AP02 on P&ID 10909001-7004. | No | 2
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE D4 : MECHANICAL: BIOREACTOR (BNRAS) WORKS | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
D4.12.3 |  | Installation, Testing and Commissioning of Bioreactor A-Recycle Pump
The installation, testing and commisioning of the A-recycle pumps includes but is not limited to: During installation ensure that the pump is alligned as well as the belt for the pulley system, check that when the pulley system rotates the pump shaft rotates as well. Ensure bearings are lubricated according to the manufacturers standard and with the recommended lubrication. The A-recycle must be a complete and working installation.
D4.12.3.1 | PEB 10.2 | Axial flow propeller pumps with fixed pitch blades for high capacity low head pumping. Fluid: Screened Sewage Rated power: 3.0kW Motor: 3 Phase, 50Hz Refer to ID tag 24-AP01, 24-AP02 on P&ID 10909001-7004. | No | 2
D4.13 |  | Manufacture, Supply and Delivery of Low Speed Mixer Baffle Plate.Refer to drawing: 10909001-6016
D4.13.1 |  | 1500 x 750 x 5 mm Thick, 304 Stainless Steel Baffle Plate, incl Equal Leg Angle, D-anchor Shackle with Rod Connector as per the engineers drawing. | No | 6
D4.13.2 |  | Installation, Testing and Commissioning of Low Speed Mixer Baffle Plate. Refer to drawing: 10909001-6016
D4.13.2.1 |  | 1500 x 750 x 5 mm Thick, 304 Stainless Steel Baffle Plate, incl Equal Leg Angle, D-anchor Shackle with Rod Connector as per the engineers drawing. | No | 6
D4.14 |  | Supply, Delivery, Installation, Testing and Commissioning of Flow Skimmer
D4.14.1 |  | Flow Skimmer | No | 1
D4.15 |  | Isolate, Decommissioning and Stripping of Bioreactor WAS Pump
D4.15.1 | PEB 10.3 | Existing submersible WAS pumps | No | 2
D4.15.2 |  | Supply and Delivery of Bioreactor WAS Pump
D4.15.2.1 | PEB 10.1 | Submersible Stainless Steel pumps for submersible installation with Vortex impeller, suitable for handling of corrosive wastewater containing solids or long-fibred material. Including discharge connection, SS Upper Guide bar bracket, SS Guide Bars (2), Leakage Monitoring Relay, SS Lifting Chain and Shackles. Duty point 1: 10 l/s @ 14m Duty point 2: 8 l/s @ 20m Motor: 3 phase 50Hz , IP68 Rated power: ±3 kW Impeller material Stainless steel Start. method: Direct on Line. Refer to ID tag 28-SP01, 28-SP02 on P&ID 10909001-7012. | No | 2
D4.15.3 |  | Installation, Testing and Commissioning of Bioreactor WAS Pump
D4.15.3.1 | PEB 10.2 | Submersible Stainless Steel pumps for submersible installation with Vortex impeller, suitable for handling of corrosive wastewater containing solids or long-fibred material. Including discharge connection, SS Upper Guide bar bracket, SS Guide Bars (2), Leakage Monitoring Relay, SS Lifting Chain and Shackles. Duty point 1: 10 l/s @ 14m Duty point 2: 8 l/s @ 20m Motor: 3 phase 50Hz , IP68 Rated power: ±3 kW Impeller material Stainless steel Start. method: Direct on Line. Refer to ID tag 28-SP01, 28-SP02 on P&ID 10909001-7012. | No | 2
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE D4 : MECHANICAL: BIOREACTOR (BNRAS) WORKS | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
D4.16 |  | Isolate, Decommissioning and Stripping of Bioreactor WAS Pipe Line and Fittings
D4.16.1 |  | DN 150 Ball Check Valve | No | 2
D4.16.2 |  | DN 150 Ductile Gate Valve | No | 2
D4.16.3 |  | DN 150 Wafer Check Valve | No | 1
D4.16.4 |  | Supply, Delivery, Installation, Testing and Commissioning of Bioreactor WAS Pipeline and Fittings.Refer to drawing: 10909001-6011
D4.16.4.1 |  | DN 80 304 Stainless Steel Piping | m | 5
D4.16.5 |  | Supply, Delivery, Installation, Testing and Commissioning of Bioreactor WAS Pipeline Fittings,Refer to drawing: 10909001-6016
D4.16.5.1 |  | DN 80 Ball Check Valve, PN 10, PN 16 Flanges, Ductile iron, NBR rubber lined ball, self cleaning, For wastewater treatment, NBR rubber O-ring, Bolt, Washer and Nut in Stainless steel, including bolt sleeve and washer kit to prevent galvanic reaction. Refer to ID tag 28-NRV01, 28-NRV02, 28-NRV03, 28-NRV04 on P&ID 10909001-7012. | No | 4
D4.16.5.2 |  | DN 80 Ductile Gate Valve, PN16, flanged with stem cap. Stainless steel Bolts, Washers and Nuts including bolt sleeve and washer kit to prevent galvanic reaction. Refer to ID tag 28-GV01, 28-GV02, 28-GV03, 28-GV04 on P&ID 10909001-7012. | No | 4
D4.16.5.3 |  | DN 50 Combination Air Release Valve, flanged. Refer to ID tag 28-ARV01, 28-ARV02 on P&ID 10909001-7012. | No | 2
D4.17 |  | Supply and Delivery of Level Probes at WAS Sump
D4.17.1 | PEI 8.1 | 3 Point Level Probe for, Low-Low Level, Low-Level and High Level including cabling, wiring to fieldbox. Refer to ID tag 28-lLSLL01, 28-LSL01,28-LSH on P&ID 10909001-7012. | No | 1
D4.17.2 | PEI 8.1 | Level Switch for Level Probe integration to MCC | No | 2
D4.17.3 |  | Supply and Delivery of Pressure Sensor on WAS Pipeline
D4.17.3.1 | PEI 8.1 | Pressure Sensor including cabling, wiring to fieldbox. Refer to ID tag 28-PSH on P&ID 10909001-7012. | No | 1
D4.17.3.2 | PEI 8.1 | Pressure Switch for Pressure Sensor integration to MCC | No | 1
D4.18 |  | Supply and Delivery of Flow Meter at WAS Outlet
D4.18.1 | PEI 8.1 | DN80~110 Clamp on Ultrasonic flow meter complete with flow sensor, converter device and transducer, data logger complete. Made in Stainless steel Includes: (a) Flow measuring sensor; (b) Converter device; (c) Data logger (d) Connection to power supply (e) All required installation cables, conduit, trunking, materials, weather-proof panels, and consumables to render a complete and working installation.Refer to ID tag 28-FE01 on P&ID 10909001-7003 | No | 1
D4.18.2 |  | Installation, Testing and Commissioning of Flow Meter at WAS Outlet
D4.18.2.1 | PEI 8.2 | DN80~110 Clamp on Ultrasonic flow meter complete with flow sensor, converter device and transducer, data logger complete. Made in Stainless steel Includes: (a) Flow measuring sensor; (b) Converter device; (c) Data logger (d) Connection to power supply (e) All required installation cables, conduit, trunking, materials, weather-proof panels, and consumables to render a complete and working installation.Refer to ID tag 28-FE01 on P&ID 10909001-7003 | No | 1
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE D4 : MECHANICAL: BIOREACTOR (BNRAS) WORKS | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
D4.19 |  | Reinstating Supports, Cleaning and Painting of Pipes ranging from DN 100 to DN 200
D4.19.1 |  | DN 100 epoxy painted, galvanised piping including supports and fittings | m | 25
D4.19.2 |  | DN 150 epoxy painted, galvanised piping including supports and fittings | m | 50
D4.19.3 |  | DN 200 epoxy painted, galvanised piping including supports and fittings | m | 50
Total Carried Forward To Summary

## Sche D5
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: VCW - TBC
|  |  | SCHEDULE D5 : MECHANICAL: CLARIFIER WORKS | SCHEDULE D5 : MECHANICAL: CLARIFIER WORKS | SCHEDULE D5 : MECHANICAL: CLARIFIER WORKS | SCHEDULE D5 : MECHANICAL: CLARIFIER WORKS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
D5 |  | SCHEDULE D5 : MECHANICAL WORK: CLARIFIER
D5.1 |  | CLARIFIER
D5.2 |  | Supply, Delivery and Installation, Testing and Commissioning of Clarifier Equipment
D5.2.1 | PEC 7.6 | Clarifier Drive Unit complete with motor, gearbox and coupling to clarifier bridge wheels. Refer to ID tag 26-EM01 on P&ID 10909001-7005. | No | 1
D5.2.1 | PEC 7.6 | Clarifier bridge driving and trailing wheels including bearings | No | 2
D5.2.1 | PEC 7.6 | V-Notch weir plate, Stainless Steel including brackets.Refer to drawing: 10909001-6007 | m | 66
D5.3 |  | Replacement of Clarifier Bridge Items
D5.3.1 | PEC 7.6 | Clarifier center bridge bearing, including center slip ring | No | 1
D5.4 |  | Supply, Delivery, Installation, Commissioning and Testing of Telescopic Weir.Refer to drawing: 10909001-6009
D5.4.1 |  | Telescopic Weir | No | 1
D5.5 |  | Complete refurbishment of Clarifier bridge structure
D5.5.1 | PEC 7.2 | Structural repair of bridge walkway, handrail, including corrosion protection. Repair,corrosion protection and allignment to ensure scraper functionality. | Sum | 1
D5.5.1 | PEC 7.6 | Replacement of scraper rubber installations | Sum | 1
D5.6 |  | RAS PUMP STATION
D5.6.1 |  | Supply and Delivery of RAS Pumps at RAS Pump Station
D5.6.1.1 | PEB 10.1 | RAS Submersible Pump. Including discharge connection, SS Upper Guide bar bracket, SS Guide Bars (2), Leakage Monitoring Relay, SS Lifting Chain and Shackles.Vortex impeller, suitable for handling of corrosive wastewater containing solids or long-fibred material. Including discharge connection, Duty point 1: 50,5 l/s @ 6m Motor: 3 phase 50Hz , IP68 Rated power: ±4,7 kW Start. method: Direct on Line. Refer to ID tag 27-SP01, 27-SP02 on P&ID 10909001-7005. | No | 2
D5.6.2 |  | Installation, Commissioning and Testing of RAS Pumps at RAS Pump Station
D5.6.2.1 | PEB 10.2 | RAS Submersible Pump. Including discharge connection, SS Upper Guide bar bracket, SS Guide Bars (2), Leakage Monitoring Relay, SS Lifting Chain and Shackles.Vortex impeller, suitable for handling of corrosive wastewater containing solids or long-fibred material. Including discharge connection, Duty point 1: 50,5 l/s @ 6m Motor: 3 phase 50Hz , IP68 Rated power: ±4,7 kW Start. method: Direct on Line. Refer to ID tag 27-SP01, 27-SP02 on P&ID 10909001-7005. | No | 2
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE D5 : MECHANICAL: CLARIFIER WORKS | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
D5.6.3 |  | Supply and Delivery of Level Probes at RAS Pump Station
D5.6.3.1 | PEI 8.1 | 4 Point Level Probe for, Low-Low Level, Low-Level, High Lever and High-High Level including cabling, wiring to fieldbox. Refer to ID tag 27-LSLL01, 27-LSL01,27-LSH01, 27-LSHH01 on P&ID 10909001-7005. | No | 1
D5.6.3.2 | PEI 8.1 | Level Switch for Level Probe integration to MCC | No | 2
D5.6.4 |  | Installation, Commissioning and Testing of Level Probes at WAS Sump
D5.6.4.1 | PEI 8.2 | 4 Point Level Probe for, Low-Low Level, Low-Level, High Lever and High-High Level including cabling, wiring to fieldbox. Refer to ID tag 27-LSLL01, 27-LSL01,27-LSH01, 27-LSHH01 on P&ID 10909001-7005. | No | 1
D5.6.4.2 | PEI 8.2 | Level Switch for Level Probe integration to MCC | No | 2
D5.6.5 |  | Isolate, Decommissioning of RAS Pump Station Pipe Line and fittings
D5.6.5.1 |  | DN 100 Ball Check Valve | No | 3
D5.6.5.2 |  | DN 100 Ductile Gate Valve Internals | No | 4
D5.6.5.3 |  | DN 25 Air Release Valve | No | 2
D5.6.6 |  | Supply, Delivery, Installation, Commissioning and Testing of RAS Pump Station Pipe Line and fittings.Refer to drawing: 10909001-6010
D5.6.6.1 |  | DN 150 Ball Check Valve, PN 10, PN16 Flanged, Ductile Iron.Stainless steel Bolts, Washers and Nuts including bolt sleeve and washer kit to prevent galvanic reaction. Refer to ID tag 27-NRV01, 27-NRV02, 27-NRV03 on P&ID 10909001-7005. | No | 2
D5.6.6.2 |  | DN 150 Ductile Gate Valve, PN 10, PN16 Flanged, Ductile Iron.Stainless steel Bolts, Washers and Nuts including bolt sleeve and washer kit to prevent galvanic reaction. | No | 3
D5.6.6.3 |  | DN 50 Combination Air Release Valve, flanged. Refer to ID tag 27-ARV01, 27-ARV02 on P&ID 10909001-7005. | No | 2
D5.6.7 |  | Supply, Delivery, Installation, Testing and Commissioning of Bioreactor RAS Pipeline and Fittings. Refer to drawing: 10909001-6010
D5.6.7.1 |  | DN 150 304 Flanged Stainless Steel Piping, including Fittings, Stainless steel Bolts, Washers, Gaskets and Nuts. | Sum | 1
D5.6.8 |  | Supply and Delivery of Material Handling, Lifting, Hoist Equipment
D5.6.8.1 |  | Manually operated chain block for a lifting capacity of 0.5 tons in accordance with SANS 1594:2007, or similar international quality standard, complete with all lifting tackle and cable required for the safe operation of the chain block. HOL to be ±6 m. Tested according to OHS ACT 85 of 1993 clause 18 and manufacturer standards/specifications, as minimum. | No | 1
D5.6.8.2 |  | Manually operated beam trolley (crawl) in accordance with SANS1824/EN13157, or similar international quality standard, with geared chain drive (plain travel) and manual brake for a lifting capacity of 0.5 tons. Beam trolley (crawl) to operate on monorail run way beam, 254x146x37, I-beam profile. Chain height at approximately 1.5m or 0.5m from floor. | No | 1
D5.6.8.3 |  | Monorail stoppers | No | 1
D5.6.8.4 |  | Stickers | No | 2
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE D5 : MECHANICAL: CLARIFIER WORKS | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
D5.6.9 |  | Installation, Testing and Commissioning of Material Handling, Lifting, Hoist Equipment
D5.6.9.1 |  | Manually operated chain block for a lifting capacity of 0.5 tons in accordance with SANS 1594:2007, or similar international quality standard, complete with all lifting tackle and cable required for the safe operation of the chain block. HOL to be ±6 m. Tested according to OHS ACT 85 of 1993 clause 18 and manufacturer standards/specifications, as minimum. | No | 1
D5.6.9.2 |  | Manually operated beam trolley (crawl) in accordance with SANS1824/EN13157, or similar international quality standard, with geared chain drive (plain travel) and manual brake for a lifting capacity of 0.5 tons. Beam trolley (crawl) to operate on monorail run way beam, 254x146x37, I-beam profile. Chain height at approximately 1.5m or 0.5m from floor. | No | 1
D5.6.9.3 |  | Monorail stoppers | No | 2
D5.6.9.4 |  | Stickers | No | 2
D5.6.9.4 |  | Touch painting/epoxy | m² | 5
Total Carried Forward To Summary

## Sche D6
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: VCW - TBC
|  |  | SCHEDULE D6 : MECHANICAL: CHLORINATION WORKS | SCHEDULE D6 : MECHANICAL: CHLORINATION WORKS | SCHEDULE D6 : MECHANICAL: CHLORINATION WORKS | SCHEDULE D6 : MECHANICAL: CHLORINATION WORKS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
D6 |  | SCHEDULE D6 : MECHANICAL WORK: CHLORINE DOSING
D6.1 |  | CHLORINE DOSING
Supply and Delivery of the Chlorine Doser
D6.1.1 |  | HTH 180KG Industrial Chip Doser. Or similar approved by the engineer. | No | 1
D6.1.2 |  | Calcium Hypochlorite in 25 kg drums | No | 64
D6.2 |  | Installation, Testing and Commissioning of the Chlorine Dosing Plant
D6.2.1 |  | HTH 180KG Industrial Chip Doser. Or similar approved by the engineer | No | 1
D6.3 |  | Supply, Delivery, Installation and Commissioning of Chlorine Dosing Pipe Line and Fittings
D6.3.1 |  | DN 25 HDPE piping including supports and fittings | m
D6.3.2 |  | DN 50 HDPE piping including supports and fittings | m
D6.3.3 |  | DN25 Rotameter Range 1000-10000L/H Refer to ID tag 31-FG01 on P&ID 10909001-7006 | No | 1
D6.3.4 |  | DN 50 Ball Valve Refer to ID tag 31-BV05 on P&ID 10909001-7006 | No | 1
D6.3.5 |  | DN 25 Diaphragm Valve Refer to ID tag 31-DV02 on P&ID 10909001-7006 | No | 1
D6.4 |  | Supply and Delivery of Material Handling, Lifting, Hoist Equipment
D6.4.1 |  | Manually operated chain block for a lifting capacity of 1 tons in accordance with SANS 1594:2007, or similar international quality standard, complete with all lifting tackle and cable required for the safe operation of the chain block. HOL to be ±3 m. Tested according to OHS ACT 85 of 1993 clause 18 and manufacturer standards/specifications, as minimum. | No | 1
D6.4.2 |  | Manually operated beam trolley (crawl) in accordance with SANS1824/EN13157, or similar international quality standard, with geared chain drive (plain travel) and manual brake for a lifting capacity of 1 tons. Beam trolley (crawl) to operate on monorail run way beam, 254x146x37, I-beam profile. Chain height at approximately 1.5m or 0.5m from floor. | No | 1
D6.4.3 |  | Monorail stoppers | No | 2
D6.4.4 |  | Stickers | No | 2
D6.5 |  | Installation, Testing and Commissioning of Material Handling, Lifting, Hoist Equipment
D6.5.1 |  | Manually operated chain block for a lifting capacity of 1 tons in accordance with SANS 1594:2007, or similar international quality standard, complete with all lifting tackle and cable required for the safe operation of the chain block. HOL to be ±3 m. Tested according to OHS ACT 85 of 1993 clause 18 and manufacturer standards/specifications, as minimum. | No | 1
D6.5.2 |  | Manually operated beam trolley (crawl) in accordance with SANS1824/EN13157, or similar international quality standard, with geared chain drive (plain travel) and manual brake for a lifting capacity of 1 tons. Beam trolley (crawl) to operate on monorail run way beam, 254x146x37, I-beam profile. Chain height at approximately 1.5m or 0.5m from floor. | No | 1
D6.5.3 |  | Monorail stoppers | No | 2
D6.5.4 |  | Stickers | No | 2
D6.5.5 |  | Touch painting/epoxy | m² | 5
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE D6 : MECHANICAL: CHLORINATION WORKS | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
D6.6 |  | FINAL EFFLUENT FLOW MEASUREMENT
D6.6.1 |  | Supply and Delivery of Effluent Flow Meter
D6.6.2 | PEI 8.1 | Ultrasonic level measurement complete with sensor, converter device and transducer, data logger complete. Made in Stainless steel Includes: (a) Sensor; (b) Converter device; (c) Data logger (d) Connection to power supply (d) All required installation cables, conduit, trunking, materials, weather-proof panels, and consumables to render a complete and working installation. Refer to ID tag 34-LE01 on P&ID 10909001-7007. | No | 1
D6.7 |  | Installation, Testing and Commissioning of Effluent Meter
D6.7.1 | PEI 8.2 | Ultrasonic level measurement complete with sensor, converter device and transducer, data logger complete. Made in Stainless steel Includes: (a) Sensor; (b) Converter device; (c) Data logger (d) Connection to power supply (d) All required installatio,n cables, conduit, trunking, materials, weather-proof panels, and consumables to render a complete and working installation. Refer to ID tag 34-LE01 on P&ID 10909001-7007. | No | 1
D6.8 |  | Ponds
D6.8.1 |  | Supply and Delivery of Water Reuse Pumps
D6.8.2 | PEB 10.1 | Water Reuse Submersible Pump. Including discharge connection, SS Upper Guide bar bracket, SS Guide Bars (2), Leakage Monitoring Relay, SS Lifting Chain and Shackles. Flow Rate: 11l/s Resulting Head: 20m Motor: 3 Phase, 50 Hz, IP55 Rated Power: ± 2kW Refer to ID tag 35-SP01,35-SP02 on P&ID 10909001-7006. | No | 2
D6.8.2 |  | Installation, Testing and Commissioning Testing of Water Reuse Pumps
D6.8.3 | PEB 10.2 | Water Reuse Submersible Pump. Including discharge connection, SS Upper Guide bar bracket, SS Guide Bars (2), Leakage Monitoring Relay, SS Lifting Chain and Shackles. Flow Rate: 11l/s Resulting Head: 20m Motor: 3 Phase, 50 Hz, IP55 Rated Power: ± 2kW Refer to ID tag 35-SP01,35-SP02 on P&ID 10909001-7006. | No | 2
D6.9 |  | Supply, Delivery, Installation, Testing and Commissioning of Water Reuse Pipe Line and Fittings.Refer to drawing: 10909001-6012-01~02
D6.9.1 |  | DN 80 Ball Check Valve, PN16, flanged,Stainless steel Bolts, Washers and Nuts including bolt sleeve and washer kit to prevent galvanic reaction. Refer to ID tag 35-NRV01, 35-NRV02 on P&ID 10909001-7006. | No | 2
D6.9.2 |  | DN 80 Ductile Gate Valve, PN16, flanged, Stainless steel Bolts, Washers and Nuts including bolt sleeve and washer kit to prevent galvanic reaction. Refer to ID tag 35-GV01, 35-GV02 on P&ID 10909001-7006. | No | 2
D6.10 |  | Supply, Delivery, Installation, Testing and Commissioning of Water Reuse Pipe Line and Fittings.Refer to drawing: 10909001-6012-01~02
D6.10.1 |  | DN 80 304 Flanged Stainless Steel Piping, including Fittings, Stainless steel Bolts, Washers, Gaskets and Nuts. | Sum | 1
D6.10.2 |  | DN 90 PE100 HDPE Piping, PN 16, including Flange Stub, 304 Stainless Steel Backing ,Fittings, Stainless steel Bolts, Washers, Gaskets and Nuts. | Sum | 1
Total Carried Forward
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
|  |  | SCHEDULE D6 : MECHANICAL: CHLORINATION WORKS | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL) | SCHEDULE B4: INLET WORKS: CONCRETE WORKS (STRUCTURAL)
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
Brought Forward
D6.11 |  | Supply and Delivery of Pressure Sensor on Water Reuse Pipeline
D6.11.1 | PEI 8.1 | Pressure Sensor including cabling, wiring to fieldbox. Refer to ID tag 35-PSH-01 on P&ID 10909001-7006. | No | 1
D6.11.2 | PEI 8.1 | Pressure Switch for Pressure Sensor integration to MCC | No | 1
D6.12 |  | Installation, Commissioning and Testing of Pressure Sensor on Water Reuse Pipeline
D6.12.1 | PEI 8.2 | Pressure Sensor including cabling, wiring to fieldbox. Refer to ID tag 35-PSH-01 on P&ID 10909001-7006. | No | 1
D6.12.2 | PEI 8.2 | Pressure Switch for Pressure Sensor integration to MCC | No | 1
Total Carried Forward To Summary

## Sche D7
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: VCW - TBC
|  |  | SCHEDULE D7 : MECHANICAL: MISCELLANEOUS WORKS | SCHEDULE D7 : MECHANICAL: MISCELLANEOUS WORKS | SCHEDULE D7 : MECHANICAL: MISCELLANEOUS WORKS | SCHEDULE D7 : MECHANICAL: MISCELLANEOUS WORKS
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
D7 |  | SCHEDULE D7 : MECHANICAL WORK: MISCELLANEOUS
D7.1 |  | OPERATION AND MAINTENANCE TEST EQUIPMENT AND CONSUMABLES
Supply and Delivery of Operation and Maintenance Test Equipment and Consumables
D7.1.1 |  | Imhoff cones and stand | No | 2
D7.1.2 |  | pH meter | No | 2
D7.1.3 |  | EC meter | No | 2
D7.1.4 |  | Spectrophotometer | No | 2
D7.1.5 |  | Chlorine Comparator | No | 2
D7.1.6 |  | Ammonia Comparator | No | 2
D7.2 |  | SLUDGE DRYING BEDS
D7.2.1 |  | Supply, Delivery, Installation, Testing and Commissioning of Sludge Drying Bed Valves, Refer to drawing: 10909001-6013
D7.2.2 |  | DN 80,Gate Valve, PN10, SS stem, SANS 1123 flanges, Ductile iron body, Face to Face dimensions according to SANS 665, EPDM rubber wedge, epoxy finish. Refer to ID tag 48-GV01, 48-GV02, 48-GV03, 48-GV04, 48-GV05, 48-GV06, 48-GV07, 48-GV08 on P&ID 10909001-7010. | No | 14
D7.2.3 |  | DN 80 304SS pipework sets, supporting Gate Valve installations, complete with flanges, fittings, incl. elbows and fixing brackets, as shown on General Arrangement | No | 14
D7.3 |  | HVAC FOR MCC ROOM, Refer to drawing: 10909001-6017
D7.3.1 |  | Supply and Delivery of the HVAC Unit
D7.3.2 |  | Air fan unit for positive pressure including speed controllable motor and filter unit constructed from pre-galvanised steel sheets with weather louvres at inlet and grilles at discharge. Primary filter element of the pleated washable type. Power: ±370W Filtered air flow capacity per fan: 0.6m3/s Motor: 230V, 50Hz ,IP54 Engineers approval required for equipment compliance with specification before procurement. | No | 3
D7.3.3 |  | Aluminium Weather Louvres with opening of 400 x 450 or similar approved | No | 6
D7.3.4 |  | Installation, Testing and Commissioning of the HVAC Unit
D7.3.5 |  | Installation costs shall encompass all mounting hardware, brackets, fixings, and ancillary components required to render a complete and working installation. Costs shall also include testing and commissioning of the unit. Air fan unit for positive pressure including speed controllable motor and filter unit constructed from pre-galvanised steel sheets with weather louvres at inlet and grilles at discharge. Primary filter element of the pleated washable type. Power: ±370W Filtered air flow capacity per fan: 0.6m3/s Motor: 230V, 50Hz ,IP54 | No | 3
D7.3.6 |  | Aluminium Weather Louvres with opening of 400 x 450 or similar approved | No | 6
Total Carried Forward To Summary

## Sche D8
TSHIAME WWTW REFURBISHMENT
SCHEDULE OF QUANTITIES
TENDER NO: VCW - TBC
|  |  | SCHEDULE D8 : MECHANICAL: SPARES | SCHEDULE D8 : MECHANICAL: SPARES | SCHEDULE D8 : MECHANICAL: SPARES | SCHEDULE D8 : MECHANICAL: SPARES
ITEM NO | PAYMENT | DESCRIPTION | UNIT | QTY | RATE | AMOUNT R
D.8 |  | SCHEDULE D8 : MECHANICAL: SPARES
D.8.1 |  | Supply, delivery and storage of mechanical spares
D8.1.1 |  | Hand Rake | No | 1
D8.1.2 |  | Hand Stop | Sum | 1
D8.1.3 |  | Pressure Sensor | No | 1
D8.1.4 |  | Pressure Gauge | No | 1
D8.1.5 |  | 1000mm Stainless Steel Level Staff Gauge | No | 1
D8.1.6 |  | Gaskets and seals for flange connection | Sum | 1
Other Provisional Sums
D8.2 |  | (a) Supply, delever and place in storage. Mechanical spares as per list of items identified by the Engineer and Employer following inputs by MaP Water. Items in (a) to include Contractor mark-up of 10% (mark-up only if non-standard item as quoted elsewhere in the schedules). | Prov Sum | 1 | 218632.9 | 218632.9
Total Carried Forward To Summary