Eskom Holdings SOC Ltd

Contract No. _________
project or contract title: REFURBISHMENT OF MEDIUM VOLTAGE MOTORS, AS STOCK ITEMS ON AN “AS AND WHEN” REQUIRED BASIS FOR A PERIOD OF FIVE YEARS AT KRIEL POWER STATION, MAIN STORES.



Part 2: Pricing Data

TSC3 Option A
	Document reference
	Title
	No of pages

	C2.1
	This cover page

Pricing assumptions: Option A
	1

2

	C2.2
	The price list 
	38


                                                                                                                                                                 41
C2.1 Pricing assumptions: Option A
1. How work is priced and assessed for payment
Clause 11 in NEC3 Term Service Contract (TSC3) core clauses and Option A states:

	Identified and defined terms
	11

11.2
	(12) The Price List is the price list unless later changed in accordance with this contract.



	
	
	(17) The Price for Services Provided to Date is the total of 
· the Price for each lump sum item in the Price List which the Contractor has completed and
· where a quantity is stated for an item in the Price List, an amount calculated by multiplying the quantity which the Contractor has completed by the rate.


	
	
	(19) The Prices are the amounts stated in the Price column of the Price List. Where a quantity is stated for an item in the Price List, the Price is calculated by multiplying the quantity by the rate.



This confirms that Option A is a priced contract where the Prices are derived from a list of items of service which can be priced as lump sums or as expected quantities of service multiplied by a rate or a mix of both.
2. Function of the Price List
Clause 54.1 in Option A states: “Information in the Price List is not Service Information”.  This confirms that instructions to do work or how it is to be done are not included in the Price List but in the Service Information.  This is further confirmed by Clause 20.1 which states, “The Contractor Provides the Service in accordance with the Service Information”. Hence the Contractor does not Provide the Service in accordance with the Price List.   The Price List is only a pricing document.  
3. Link to the Contractor’s plan
Clause 21.4 states “The Contractor provides information which shows how each item description on the Price List relates to the operations on each plan which he submits for acceptance”.  Hence when compiling the price list, the tendering contractor needs to develop his first clause 21.2 plan in such a way that operations shown on it can be priced in the price list  and result in a satisfactory cash flow in terms of clause 11.2(17). 

4. Preparing the price list
Before preparing the price list, both the Employer and tendering contractors should read the TSC3 Guidance Notes pages 14 and 15.  In an Option A contract, either Party may have entered items into the price list either as a process of offer and acceptance (tendering) or by negotiation depending on the nature of the service to be provided.  Alternatively the Employer, in his Instructions to Tenderers or in a Tender Schedule, may have listed some items that he requires the Contractor to include in the price list to be prepared and priced by him. 

It is assumed that in preparing or finalising the price list the Contractor:
· Has taken account of the guidance given in the TSC3 Guidance Notes relevant to Option A;

· Understands the function of the Price List and how work is priced and paid for;

· Is aware of the need to link operations shown in his plan to items shown in the Price List;
· Has listed and priced items in the price list which are inclusive of everything necessary and incidental to Providing the Service in accordance with the Service Information, as it was at the time of tender, as well as correct any Defects not caused by an Employer’s risk;
· Has priced work he decides not to show as a separate item within the Prices or rates of other listed items in order to fulfil the obligation to complete the service for the tendered total of the Prices. 
· Understands there is no adjustment to items priced as lump sums if the amount, or quantity, of work within that item later turns out to be different to that which the Contractor estimated at time of tender. The only basis for a change to the (lump sum) Prices is as a result of a compensation event. 
4.1. Format of the price list
(From the example given in an Appendix within the TSC3 Guidance Notes)
Entries in the first four columns in the price list in section C2.2 are made either by the Employer or the tendering contractor. 

If the Contractor is to be paid an amount for the item which is not adjusted if the quantity of work in the item changes, the tendering contractor enters the amount in the Price column only, the Unit, Expected Quantity and Rate columns being left blank.

If the Contractor is to be paid an amount for an item of work which is the rate for the work multiplied by the quantity completed, the tendering contractor enters the rate which is then multiplied by the Expected Quantity to produce the Price, which is also entered.
If the Contractor is to be paid a Price for an item proportional to the length of time for which a service is provided, a unit of time is stated in the Unit column and the expected length of time (as a quantity of the stated units of time) is stated in the Expected Quantity column.

C2.2 the price list
	Motor Description: Electric feed pump (EFP) motor: 141271
	Output 

Power (kW)10 000
	Voltage (V)

11kV
	Current (A) 

601 A
	Speed (rpm)

1492
	Weight 

35 Ton


	No.
	Description
	Estimated Quantity Rate
	 Breakdown Rate 
	Total
	Estimated  Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	
	
	
	50
	5

	2
	Dismantle, clean, test & assess all parts. Perform Non-Destructive Testing on the rotor shaft.  Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, El-Cid, Bar to bar continuity, core flux test, Tan delta testing
	
	
	
	50
	5

	3
	Overhaul stator & spray with insulating varnish
	
	
	
	50
	5

	4
	Overhaul rotor & spray with insulating varnish.
	
	
	
	50
	5

	5
	Polish DE&NDE bearings
	
	
	
	50
	5

	6
	Re-metal bearing (price per bearing) 250mm GB bearing
	
	
	
	80
	10

	7
	Replacement of bearing seals (Labyrinth seals on GB bearings)
	
	
	
	106
	20

	8
	Replace oil ring (Price per ring)
	
	
	
	20
	5

	9
	Re-metal bearing (price per bearing) 250mm Michelle bearing
	
	
	
	50
	10

	10
	Replacement of bearing seals (felt seals on Michelle bearings)
	
	
	
	106
	20

	11
	Clean and paint bearing housings - Price per housing
	
	
	
	50
	5

	12
	Replace bearing insulation - Price per bearing
	
	
	
	100
	10

	13
	Replacement of oil sight glasses to OEM standard (glass)
	
	
	
	6
	2

	14
	Polish journals (price per journal)
	
	
	
	50
	5

	15
	Polish Seal landing (price per seal landing)
	
	
	
	50
	5

	16
	Overhaul & clean heat exchangers
	
	
	
	50
	5

	17
	Repair heat exchanger
	
	
	
	10
	2

	18
	Supply and fit new ZORC (11kVA)
	
	
	
	30
	5

	19
	Supply and fit new terminal box and cover
	
	
	
	5
	2

	20
	Supply and fit 1xheater box
	
	
	
	5
	5

	21
	Supply and fit 2xforce feed pipes NDE
	
	
	
	5
	2

	22
	Supply and fit 2xforce feed pipes DE
	
	
	
	5
	2

	23
	Supply and fit 2x flow meters
	
	
	
	10
	2

	24
	Micro-weld and machine DE &NDE bearing journals
	
	
	
	50
	5

	25
	Supply new coupling
	
	
	
	5
	2

	26
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	
	
	
	50
	5

	27
	Replacement of line side leads (price per lead)
	
	
	
	5
	2

	28
	Replacement of star side leads (price per lead)
	
	
	
	5
	2

	29
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	
	
	
	50
	5

	30
	Polish stator feet
	
	
	
	50
	5

	31
	Reassemble motor complete
	
	
	
	50
	5

	32
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (11kV) for the duration of the test
	
	
	
	50
	5

	33
	Paint the motors light grey (gloss enamel G29)
	
	
	
	50
	5

	34
	Fit the shaft locking device
	
	
	
	50
	5

	35
	Return the motor back to site (Kriel Power Station)
	
	
	
	50
	5

	Rewind

	36
	Rewind stator
	 
	 
	 
	8
	2

	37
	Re-bar rotor
	 
	 
	 
	3
	2

	38
	New stator core
	 
	 
	 
	2
	1

	TOTAL 
	 
	 


2. 

	Motor Description: Forced Draught Fan(FD) motor: 141233
	Output 

Power (kW)

3050
	Voltage (V)

3.3 kV
	Current (A) 

636 A
	Speed (rpm)

741
	Weight 

20 Ton


	No.
	Description
	Estimated Quantity Rate
	 Breakdown Rate 
	Total
	Estimated Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	30
	2

	2
	Dismantle, clean, test & assess all parts. Perform Non-Destructive Testing on the rotor shaft.  Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	30
	2

	3
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	30
	2

	4
	Overhaul rotor & spray with insulating varnish.
	 
	 
	 
	30
	2

	5
	Polish DE&NDE bearings
	 
	 
	 
	30
	2

	6
	Re-metal bearing (price per bearing) 225mm Renk bearing
	 
	 
	 
	36
	6

	7
	Replacement of bearing seals (Labyrinth seals on Renk bearings)
	 
	 
	 
	60
	20

	8
	Clean and paint bearing housings
	 
	 
	 
	30
	2

	9
	Replace bearing insulation (Price per bearing)
	 
	 
	 
	20
	2

	10
	Replacement of oil sight glasses to OEM standard (glass)
	 
	 
	 
	6
	2

	11
	Polish journals (Price per journal)
	 
	 
	 
	30
	4

	12
	Polish seal landings (Price per seal landing)
	 
	 
	 
	30
	4

	13
	Overhaul & clean heat exchangers
	 
	 
	 
	30
	2

	14
	Repair heat exchanger
	 
	 
	 
	2
	1

	15
	Supply and fit new terminal box and cover
	 
	 
	 
	1
	0

	16
	Supply and fit 1xheater box
	 
	 
	 
	2
	0

	17
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	30
	2

	18
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	30
	2

	19
	Replacement of line side leads (price per lead)
	 
	 
	 
	2
	0

	20
	Replacement of star side leads (price per lead)
	 
	 
	 
	2
	0

	21
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	30
	2

	22
	Reassemble motor
	 
	 
	 
	30
	2

	23
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	30
	2

	24
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	30
	2

	25
	Fit the shaft locking device
	 
	 
	 
	30
	2

	26
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	30
	2

	Rewind

	27
	Rewind stator
	 
	 
	 
	2
	0

	28
	Re-bar rotor
	 
	 
	 
	1
	1

	29
	New stator core
	 
	 
	 
	1
	1

	TOTAL 
	 
	 


3. 

	Motor Description: Induced Draught Fan(ID) Motor: 141234
	Output 

Power (kW) 2500
	Voltage (V)

3.3 kV
	Current (A) 

538 A
	Speed (rpm)

597
	Weight 

20 Ton


	No.
	Description
	Estimated Quantity Rate
	 Breakdown Rate 
	Total
	Estimated Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	30
	2

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, El-Cid, Bar to bar continuity, core flux test, Tan delta testing
	 
	 
	 
	30
	2

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	30
	2

	4
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	30
	2

	5
	Overhaul rotor & spray with insulating varnish.
	 
	 
	 
	30
	2

	6
	Polish DE&NDE bearings
	 
	 
	 
	30
	4

	7
	Re-metal bearing (price per bearing) 200mm Renk bearing
	 
	 
	 
	60
	12

	8
	Replacement of bearing seals (Labyrinth seals on Renk bearings)
	 
	 
	 
	60
	12

	9
	Clean and paint bearing housings
	 
	 
	 
	40
	4

	10
	Replace bearing insulation
	 
	 
	 
	40
	6

	11
	Replacement of oil sight glasses to OEM standard (glass)
	 
	 
	 
	3
	2

	12
	Polish journals (Price per journal)
	 
	 
	 
	30
	4

	13
	Polish seal landings (Price per seal landing)
	 
	 
	 
	30
	4

	14
	Overhaul and clean heat exchanger
	 
	 
	 
	30
	4

	15
	Repair heat exchanger
	 
	 
	 
	4
	2

	16
	Supply and fit new terminal box and cover
	 
	 
	 
	4
	1

	17
	Supply and fit 1xheater box
	 
	 
	 
	2
	3

	18
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	30
	4

	19
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	30
	4

	20
	Replacement of line side leads (price per lead)
	 
	 
	 
	6
	2

	21
	Replacement of star side leads (price per lead)
	 
	 
	 
	6
	2

	22
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	30
	2

	23
	Reassemble motor
	 
	 
	 
	30
	2

	24
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	30
	2

	25
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	30
	2

	26
	Fit the shaft locking device
	 
	 
	 
	30
	2

	27
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	30
	2

	Rewind

	28
	Rewind stator
	 
	 
	 
	2
	1

	29
	Re-bar rotor
	 
	 
	 
	1
	1

	30
	New stator core
	 
	 
	 
	1
	1

	TOTAL 
	 
	 


4. 

	Motor Description: PA fan (U1-3)Motor: 179099
	Output 

Power (kW)465
	Voltage (V)

3.3 kV
	Current (A) 

98 A
	Speed (rpm)

1492
	Weight 

4.5 Ton


	No.
	Description
	 Estimated Quantity Rate 
	 Breakdown Rate 
	Total
	Estimated Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	70
	8

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	70
	8

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	70
	8

	4
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	70
	8

	5
	Overhaul rotor & spray with insulating varnish.
	 
	 
	 
	70
	8

	6
	Polish DE&NDE bearings
	 
	 
	 
	70
	8

	7
	Re-metal bearing (price per bearing) 110mm GB bearing
	 
	 
	 
	140
	16

	8
	Replacement of bearing seals (Labyrinth seals on GB bearings)
	 
	 
	 
	140
	16

	9
	Clean and paint bearing housings
	 
	 
	 
	70
	8

	10
	Replace bearing insulation
	 
	 
	 
	40
	6

	11
	Replacement of all oil sight glasses to OEM standard (glass)
	 
	 
	 
	4
	2

	12
	Polish journals (Price per journal)
	 
	 
	 
	70
	24

	13
	Polish seal landings (Price per seal landing
	 
	 
	 
	70
	24

	14
	Overhaul & clean heat exchangers
	 
	 
	 
	70
	12

	15
	Repair heat exchanger 
	 
	 
	 
	5
	2

	16
	Replacement of cooling fans
	 
	 
	 
	3
	1

	17
	Supply and fit new terminal box and cover
	 
	 
	 
	4
	2

	18
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	70
	8

	19
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	70
	8

	20
	Replacement of line side leads (price per lead)
	 
	 
	 
	5
	2

	21
	Replacement of star side leads (price per lead)
	 
	 
	 
	5
	2

	22
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	70
	8

	23
	Polish stator feet
	 
	 
	 
	70
	8

	24
	Reassemble motor
	 
	 
	 
	70
	8

	25
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	70
	8

	26
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	70
	8

	27
	Fit the shaft locking device
	 
	 
	 
	70
	8

	28
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	70
	8

	Rewind
	 
	 
	 

	29
	Rewind stator
	 
	 
	 
	6
	3

	30
	Re-bar rotor
	 
	 
	 
	3
	2

	31
	New stator core
	 
	 
	 
	2
	1

	TOTAL 
	 
	 


5. 

	Motor Description: PA fan (U4-6) Motor: 179096
	Output 

Power (kW) 650
	Voltage (V)

3.3 kV
	Current (A) 

113 A
	Speed (rpm)

1488
	Weight 

5 Ton


	No.
	Description
	 Estimated Quantity Rate 
	 Breakdown Rate 
	Total
	Estimated  Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	50
	5

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	50
	5

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	50
	5

	4
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	50
	5

	5
	Overhaul rotor & spray with insulating varnish.
	 
	 
	 
	50
	5

	6
	Polish DE&NDE bearings
	 
	 
	 
	100
	10

	7
	Re-metal bearing (price per bearing) 100mm GB bearing
	 
	 
	 
	100
	10

	8
	Replacement of bearing seals (Labyrinth seals)
	 
	 
	 
	100
	10

	9
	Install new oil scoop kits
	 
	 
	 
	20
	5

	10
	Clean and paint bearing housings
	 
	 
	 
	100
	5

	11
	Replace bearing insulation
	 
	 
	 
	100
	10

	12
	Replacement of all oil sight glasses to OEM standard (glass)
	 
	 
	 
	6
	2

	13
	Polish journals and seal landings
	 
	 
	 
	50
	10

	14
	Overhaul & clean heat exchangers
	 
	 
	 
	20
	5

	15
	Repair heat exchanger
	 
	 
	 
	3
	2

	16
	Replacement of cooling fans
	 
	 
	 
	3
	1

	17
	Supply and fit new terminal box and cover
	 
	 
	 
	4
	2

	18
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	50
	5

	19
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	50
	5

	20
	Replacement of line side leads (price per lead)
	 
	 
	 
	4
	2

	21
	Replacement of star side leads (price per lead)
	 
	 
	 
	4
	2

	22
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	50
	5

	23
	Polish stator feet
	 
	 
	 
	50
	5

	24
	Reassemble motor complete
	 
	 
	 
	50
	5

	25
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	50
	5

	26
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	50
	5

	27
	Fit the shaft locking device
	 
	 
	 
	50
	5

	28
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	50
	5

	Rewind

	29
	Rewind stator
	 
	 
	 
	4
	2

	30
	Re-bar rotor
	 
	 
	 
	2
	2

	31
	New stator core
	 
	 
	 
	1
	0

	TOTAL 
	 
	 


6.

	Motor Description: Mill (U1-3) Motor: 141218
	Output 

Power (kW)328
	Voltage (V)

3.3 kV
	Current (A) 

74 A
	Speed (rpm)

938
	Weight 

4.5 Ton


	No.
	Description
	 Estimated Quantity Rate 
	 Breakdown Rate 
	Total
	Estimated  Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	80
	20

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	80
	20

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	80
	20

	4
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	80
	20

	5
	Overhaul rotor & spray with insulating varnish.
	 
	 
	 
	80
	20

	6
	Polish DE&NDE bearings
	 
	 
	 
	80
	20

	7
	Re-metal bearing (price per bearing) 110mm GB bearing
	 
	 
	 
	160
	40

	8
	Replacement of bearing seals (Labyrinth seals)
	 
	 
	 
	160
	40

	9
	Re-metal bearing (price per bearing) 4½ inch Glacier bearing
	 
	 
	 
	160
	40

	10
	Install new oil scoop kits
	 
	 
	 
	20
	12

	11
	Clean and paint bearing housings
	 
	 
	 
	160
	40

	12
	Replace bearing insulation
	 
	 
	 
	160
	40

	13
	Replacement of oil sight glasses to OEM standard (glass)
	 
	 
	 
	60
	18

	14
	Polish journals and seal landings
	 
	 
	 
	80
	20

	15
	Overhaul & clean heat exchangers
	 
	 
	 
	80
	20

	16
	Repair heat exchanger
	 
	 
	 
	10
	2

	17
	Replacement of cooling fans
	 
	 
	 
	3
	1

	18
	Supply and fit new terminal box and cover
	 
	 
	 
	4
	2

	19
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	80
	20

	20
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	80
	20

	21
	Replacement of line side leads (price per lead)
	 
	 
	 
	10
	5

	22
	Replacement of star side leads (price per lead)
	 
	 
	 
	10
	5

	23
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	80
	20

	24
	Polish stator feet
	 
	 
	 
	80
	20

	25
	Reassemble motor complete
	 
	 
	 
	80
	20

	26
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test.
	 
	 
	 
	80
	20

	27
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	80
	20

	28
	Fit the shaft locking device
	 
	 
	 
	80
	20

	29
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	80
	20

	Rewind

	30
	Rewind stator
	 
	 
	 
	12
	6

	31
	Re-bar rotor
	 
	 
	 
	6
	4

	32
	New stator core
	 
	 
	 
	2
	2

	TOTAL 
	 
	 


7. 

	Motor Description: Mill (U4-6) Motor: 179095
	Output 

Power (kW)570
	Voltage (V)

3.3 kV
	Current (A) 

130 A
	Speed (rpm)

986
	Weight 

5.5 Ton


	No.
	Description
	 Estimated Quantity Rate 
	 Breakdown Rate 
	Total
	Estimated Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	40
	6

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	40
	6

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	40
	6

	4
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	40
	6

	5
	Overhaul rotor & spray with insulating varnish.
	 
	 
	 
	40
	6

	6
	Polish DE&NDE bearings
	 
	 
	 
	40
	6

	7
	Re-metal bearing (price per bearing) 140mm GB bearing
	 
	 
	 
	80
	12

	8
	Replacement of bearing seals (Labyrinth seals)
	 
	 
	 
	80
	48

	9
	Re-metal bearing (price per bearing) 5 inch Glacier bearing
	 
	 
	 
	80
	10

	10
	Install new oil scoop kits
	 
	 
	 
	30
	4

	11
	Clean and paint bearing housings
	 
	 
	 
	60
	12

	12
	Replace bearing insulation
	 
	 
	 
	100
	8

	13
	Replacement of oil sight glasses to OEM standard (glass)
	 
	 
	 
	40
	12

	14
	Polish journals and seal landings
	 
	 
	 
	40
	12

	15
	Overhaul & clean heat exchangers
	 
	 
	 
	40
	12

	16
	Repair heat exchanger
	 
	 
	 
	10
	2

	17
	Replacement of cooling fans
	 
	 
	 
	3
	1

	18
	Supply and fit new terminal box and cover
	 
	 
	 
	5
	2

	19
	Supply and fit 1xheater box
	 
	 
	 
	6
	2

	20
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	40
	12

	21
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	40
	6

	22
	Replacement of line side leads (price per lead)
	 
	 
	 
	4
	2

	23
	Replacement of star side leads (price per lead)
	 
	 
	 
	6
	2

	24
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	40
	12

	25
	Polish stator feet
	 
	 
	 
	40
	6

	26
	Reassemble motor complete
	 
	 
	 
	40
	6

	27
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	40
	6

	28
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	40
	6

	29
	Fit the shaft locking device
	 
	 
	 
	40
	6

	30
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	40
	6

	Rewind
	 
	 
	 

	31
	Rewind stator
	 
	 
	 
	6
	3

	32
	Re-bar rotor
	 
	 
	 
	4
	2

	33
	New stator core
	 
	 
	 
	2
	1

	TOTAL 
	 
	 


8. 

	Motor Description: Condensate Extraction Pump (CEP) motor: Vertical: 179098
	Output 

Power (kW)1500
	Voltage (V)

3.3 kV
	Current (A) 

310 A
	Speed (rpm)

1488
	Weight 

6 Ton


	No.
	Description
	Estimated Quantity Rate
	 Breakdown Rate 
	Total
	Estimated Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	45
	5

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	45
	5

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	45
	5

	4
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	45
	5

	5
	Overhaul rotor & spray with insulating varnish
	 
	 
	 
	45
	5

	6
	Polish NDE guide bearing
	 
	 
	 
	90
	5

	7
	Polish thrust pads
	 
	 
	 
	45
	5

	8
	Re-metal 110mm Federal Mogul thrust & guide bearing
	 
	 
	 
	45
	5

	9
	Polish DE bearing journal
	 
	 
	 
	45
	5

	10
	Replace NDE bearing - SKF 7324 angular contact bearing
	 
	 
	 
	45
	5

	11
	Replace DE bearing - SKF 6330 deep groove ball bearing
	 
	 
	 
	45
	5

	12
	Clean, overhaul and paint bearing housings
	 
	 
	 
	45
	10

	13
	Pressure test bearing cooler
	 
	 
	 
	20
	5

	14
	Overhaul & clean bearing cooler
	 
	 
	 
	20
	5

	15
	Supply new bearing cooler
	 
	 

	 
	5
	2

	16
	Supply and fit new terminal box and cover
	 
	 
	 
	2
	0

	17
	Supply and fit 1xheater box
	 
	 
	 
	2
	0

	18
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	80
	6

	19
	Supply new coupling
	 
	 
	 
	10
	2

	20
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	45
	5

	21
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	45
	5

	22
	Polish stator feet and conduct concentricity tests
	 
	 
	 
	45
	5

	23
	Reassemble motor
	 
	 
	 
	45
	5

	24
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	45
	5

	25
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	45
	5

	26
	Fit the shaft locking device
	 
	 
	 
	45
	5

	27
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	45
	5

	Rewind
	 
	 
	 

	28
	Rewind stator
	 
	 
	 
	8
	3

	29
	Re-bar rotor
	 
	 
	 
	3
	1

	30
	New stator core
	 
	 
	 
	2
	0

	TOTAL 
	 
	 


9.

	Motor Description: Cooling water (CW) pump motor: vertical:179097
	Output 

Power (kW)1500
	Voltage (V)

3.3 kV
	Current (A) 

340 A
	Speed (rpm)

330
	Weight 

20 Ton


	No.
	Description
	Estimated Quantity Rate
	 Breakdown Rate 
	Total
	Estimated Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	25
	2

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, El-Cid, Bar to bar continuity, core flux test, Tan delta testing
	 
	 
	 
	25
	2

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	25
	2

	4
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	25
	2

	5
	Overhaul rotor & spray with insulating varnish.
	 
	 
	 
	25
	2

	6
	Polish NDE bearing
	 
	 
	 
	25
	2

	7
	Polish thrust pads
	 
	 
	 
	25
	2

	8
	Polish NDE bearing journal
	 
	 
	 
	25
	2

	9
	Clean, overhaul and paint NDE bearing housing
	 
	 
	 
	25
	2

	10
	Polish DE bearing
	 
	 
	 
	25
	2

	11
	Polish DE bearing journal
	 
	 
	 
	25
	2

	12
	Clean, overhaul and paint DE bearing housing
	 
	 
	 
	25
	2

	13
	Pressure test bearing cooler
	 
	 
	 
	25
	2

	14
	Overhaul & clean bearing cooler
	 
	 
	 
	25
	2

	15
	Supply new bearing cooler
	 
	 
	 
	5
	2

	16
	Supply and fit new terminal box and cover
	 
	 
	 
	5
	2

	17
	Supply and fit 1xheater box
	 
	 
	 
	5
	2

	18
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	50
	4

	19
	Supply new coupling
	 
	 
	 
	5
	2

	20
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	25
	2

	21
	Swap Coupling
	 
	 
	 
	25
	2

	22
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	25
	2

	23
	Polish stator feet and conduct concentricity tests
	 
	 
	 
	25
	6

	24
	Reassemble motor
	 
	 
	 
	25
	6

	25
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	25
	6

	26
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	25
	6

	27
	Fit the shaft locking device
	 
	 
	 
	25
	6

	28
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	25
	6

	Rewind

	29
	Rewind stator
	 
	 
	 
	3
	0

	30
	Re-bar rotor
	 
	 
	 
	2
	0

	31
	New stator core
	 
	 
	 
	1
	0

	TOTAL 
	 
	 


10.

	Motor Description: Ash pump motor: 217674


	Output 

Power (kW)420
	Voltage (V)

3.3 kV
	Current (A) 

87 A
	Speed (rpm)

1481
	Weight 

3 Ton


	No.
	Description
	 Estimated Quantity Rate 
	 Breakdown Rate 
	Total
	Estimated Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	80
	15

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	80
	15

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	80
	15

	4
	Polish stator feet
	 
	 
	 
	80
	15

	5
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	80
	15

	6
	Overhaul rotor & spray with insulating varnish
	 
	 
	 
	80
	15

	7
	Supply and fit new DE and NDE "V" Seals (V90)
	 
	 
	 
	160
	30

	8
	Supply and fit DE bearings-NU219 & 6219 C3
	 
	 
	 
	80
	30

	9
	Supply and fit NDE bearing NU219 C3
	 
	 
	 
	80
	15

	10
	Supply and fit new ZORC (3.3 kVA)
	 
	 
	 
	30
	10

	11
	Supply and fit new terminal box and cover
	 
	 
	 
	5
	15

	12
	Supply and fit 1xheater box
	 
	 
	 
	5
	15

	13
	Supply new fan 
	 
	 
	 
	50
	15

	14
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	80
	15

	15
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	80
	15

	16
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	80
	15

	17
	Reassemble motor
	 
	 
	 
	80
	15

	18
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	80
	15

	19
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	80
	15

	20
	Fit the shaft locking device
	 
	 
	 
	80
	15

	21
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	80
	15

	Rewind

	22
	Rewind stator
	 
	 
	 
	15
	10

	23
	Re-bar rotor
	 
	 
	 
	8
	4

	24
	New stator core
	 
	 
	 
	6
	2

	TOTAL 
	 
	 


11. 

	Motor Description: Sluice pump motor: 141279
	Output 

Power (kW)300
	Voltage (V)

3.3 kV
	Current (A) 

63 A
	Speed (rpm)

1477
	Weight 

3 Ton


	No.
	Description
	 Estimated  Quantity Rate 
	 Breakdown Rate 
	Total
	Estimated  Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	45
	8

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	45
	8

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	45
	8

	4
	Polish stator feet
	 
	 
	 
	45
	8

	5
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	45
	8

	6
	Overhaul rotor & spray with insulating varnish
	 
	 
	 
	45
	8

	7
	Supply DE and NDE "V" Seals (V100)
	 
	 
	 
	45
	8

	8
	Supply and fit DE bearings- NU 322 C3
	 
	 
	 
	45
	8

	9
	Supply and fit NDE bearing 6219 C3
	 
	 
	 
	45
	8

	10
	Supply and fit new ZORC (3.3 kVA)
	 
	 
	 
	15
	4

	11
	Supply and fit new terminal box and cover
	 
	 
	 
	5
	2

	12
	Supply and fit 1xheater box
	 
	 
	 
	5
	2

	13
	Supply new fan 
	 
	 
	 
	45
	8

	14
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	45
	16

	15
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	45
	8

	16
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	45
	8

	17
	Reassemble motor
	 
	 
	 
	45
	8

	18
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	45
	8

	19
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	45
	8

	20
	Fit the shaft locking device
	 
	 
	 
	45
	8

	21
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	45
	8

	Rewind

	22
	Rewind stator
	 
	 
	 
	8
	3

	23
	Re-bar rotor
	 
	 
	 
	4
	2

	24
	New stator core
	 
	 
	 
	2
	1

	TOTAL 
	 
	 


12.

	Motor Description: Centac Compressor motor: 501009
	Output 

Power (kW)530
	Voltage (V)

3.3 kV
	Current (A) 

109 A
	Speed (rpm)

2969
	Weight 

3 Ton


	No.
	Description
	Estimated Quantity Rate
	 Breakdown Rate 
	Total
	Estimated  Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	6
	3

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	6
	3

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	6
	3

	4
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	6
	3

	5
	Overhaul rotor & spray with insulating varnish.
	 
	 
	 
	6
	3

	6
	Re-metal 80mm Glacier bearings
	 
	 
	 
	6
	3

	7
	Replacement of motor bearing seals (Labyrinth seals)
	 
	 
	 
	12
	6

	8
	Supply new breathers and sight glasses
	 
	 
	 
	3
	2

	9
	Overhaul & clean heat exchangers
	 
	 
	 
	6
	3

	10
	Supply and fit new terminal box and cover
	 
	 
	 
	3
	2

	11
	Supply and fit 1xheater box
	 
	 
	 
	3
	2

	12
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	6
	3

	13
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	6
	3

	14
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	6
	3

	15
	Reassemble motor
	 
	 
	 
	6
	3

	16
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test.
	 
	 
	 
	6
	3

	17
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	6
	3

	18
	Fit the shaft locking device
	 
	 
	 
	6
	3

	19
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	6
	3

	Rewind

	20
	Rewind stator
	 
	 
	 
	2
	1

	21
	Re-bar rotor
	 
	 
	 
	1
	1

	22
	New stator core
	 
	 
	 
	1
	1

	TOTAL 
	 
	 


13.

	Motor Description:Demag Compressor motor: 500980


	Output 

Power (kW)650
	Voltage (V)

3.3 kV
	Current (A) 

136 A
	Speed (rpm)

2955
	Weight 

3.5 Ton


	No.
	Description
	Estimated Quantity Rate
	 Breakdown Rate 
	Total
	Estimated  Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	6
	3

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	6
	3

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	6
	3

	4
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	6
	3

	5
	Overhaul rotor & spray with insulating varnish.
	 
	 
	 
	6
	3

	6
	Re-metal 80mm Glacier bearings
	 
	 
	 
	6
	3

	7
	Replacement of motor bearing seals (Labyrinth seals) - 100mm
	 
	 
	 
	12
	6

	8
	Supply new breathers and sight glasses
	 
	 
	 
	6
	3

	9
	Supply and fit new terminal box and cover
	 
	 
	 
	3
	1

	10
	Supply and fit 1xheater box
	 
	 
	 
	3
	1

	11
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	6
	3

	12
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	6
	3

	13
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	6
	3

	14
	Reassemble motor
	 
	 
	 
	6
	3

	15
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	6
	3

	16
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	6
	3

	17
	Fit the shaft locking device
	 
	 
	 
	6
	3

	18
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	6
	3

	Rewind

	19
	Rewind stator
	 
	 
	 
	2
	2

	20
	Re-bar rotor
	 
	 
	 
	1
	1

	21
	New stator core
	 
	 
	 
	1
	1

	TOTAL 
	 
	 


14.

	Motor Description: Cameron Compressor motor: 664141
	Output 

Power (kW)510
	Voltage (V)

3.3 kV
	Current (A) 

102 A
	Speed (rpm)

2969
	Weight 

3 Ton


	No.
	Description
	 Estimated Quantity Rate 
	 Breakdown Rate 
	Total
	Estimated Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	10
	2

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	10
	2

	3
	Perform NDT on the rotor shaft and provide feedback on the condition of the motor
	 
	 
	 
	10
	2

	4
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	10
	2

	5
	Overhaul rotor & spray with insulating varnish
	 
	 
	 
	10
	2

	6
	Re-metal 80mm Glacier bearings
	 
	 
	 
	10
	2

	7
	Replacement of motor bearing seals (Labyrinth seals)
	 
	 
	 
	20
	4

	8
	Supply new breather and sight glasses
	 
	 
	 
	5
	2

	9
	Supply and fit new terminal box and cover
	 
	 
	 
	5
	2

	10
	Supply and fit 1xheater box
	 
	 
	 
	4
	2

	11
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	10
	2

	12
	Dynamically balance the rotor at operating speed according to ISO 1940/01 Balancing grade G6.3 (balancing certificate to be included in test report)
	 
	 
	 
	10
	2

	13
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	10
	2

	14
	Re-assemble motor
	 
	 
	 
	10
	2

	15
	Test run the motor in the presence of an Eskom representative and submit report. Motor to be at full voltage (3.3kV) for the duration of the test
	 
	 
	 
	10
	2

	16
	Paint the motor light grey (gloss enamel G29)
	 
	 
	 
	10
	2

	17
	Fit the shaft locking device
	 
	 
	 
	10
	2

	18
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	10
	2

	Rewind

	19
	Rewind stator
	 
	 
	 
	3
	2

	20
	Re-bar rotor
	 
	 
	 
	2
	2

	21
	New stator core
	 
	 
	 
	2
	1

	TOTAL 
	 
	 


15.
	Motor Description: HP Demin motor:614532
	Output 

Power (kW)160
	Voltage (V)

3.3 kV
	Current (A) 

36 A
	Speed (rpm)

1484
	Weight 

2 Ton


	No.
	Description
	Estimated Quantity Rate
	 Breakdown Rate 
	Total
	Estimated Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	10
	2

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	10
	2

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	10
	2

	4
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	10
	2

	5
	Overhaul rotor & spray with insulating varnish.
	 
	 
	 
	10
	2

	6
	Supply DE and NDE "V" Seals (V90)
	 
	 
	 
	10
	2

	7
	Supply and fit DE bearings - 6320 C3
	 
	 
	 
	10
	2

	8
	Supply and fit NDE bearing - 6316 C3
	 
	 
	 
	10
	2

	9
	Supply and fit new terminal box and cover
	 
	 
	 
	4
	2

	10
	Supply and fit 1xheater box
	 
	 
	 
	4
	2

	11
	Supply new fan
	 
	 
	 
	4
	2

	12
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	10
	2

	13
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	10
	2

	14
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	10
	2

	15
	Reassemble motor
	 
	 
	 
	10
	2

	16
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	10
	2

	17
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	10
	2

	18
	Fit the shaft locking device
	 
	 
	 
	10
	2

	19
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	10
	2

	Rewind

	20
	Rewind stator
	
	
	
	3
	1

	21
	Re-bar rotor
	
	
	
	1
	1

	22
	New stator core
	
	
	
	1
	1

	TOTAL 
	 
	 


16.

	Motor Description: Ash water return (small) motor: 141329


	Output 

Power (kW)300
	Voltage (V)

3.3 kV
	Current (A) 

55 A
	Speed (rpm)

1484
	Weight 

2.5 Ton


	No.
	Description
	 Estimated Quantity Rate
	 Breakdown Rate 
	Total
	Estimated  Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	10
	3

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	10
	3

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	10
	3

	4
	Polish stator feet
	 
	 
	 
	10
	3

	5
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	10
	3

	6
	Overhaul rotor & spray with insulating varnish
	 
	 
	 
	10
	3

	7
	Supply DE and NDE "V" Seals 
	 
	 
	 
	10
	3

	8
	Supply and fit DE bearings - NU 322
	 
	 
	 
	10
	3

	9
	Supply and fit NDE bearing - 6318
	 
	 
	 
	10
	3

	10
	Re-sleeve DE bearing housing
	 
	 
	 
	10
	3

	11
	Re-sleeve NDE bearing housing
	 
	 
	 
	10
	3

	12
	Supply and fit new terminal box and cover
	 
	 
	 
	4
	2

	13
	Supply and fit 1xheater box
	 
	 
	 
	4
	2

	14
	Supply new fan 
	 
	 
	 
	4
	2

	15
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	10
	3

	16
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	10
	3

	17
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	10
	3

	18
	Replace all grease pipes and fittings
	 
	 
	 
	10
	3

	19
	Reassemble motor
	 
	 
	 
	10
	3

	20
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	10
	3

	21
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	10
	3

	22
	Fit the shaft locking device
	 
	 
	 
	10
	3

	23
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	10
	3

	Rewind

	24
	Rewind stator
	 
	 
	 
	4
	2

	25
	Re-bar rotor
	 
	 
	 
	2
	1

	26
	New stator core
	 
	 
	 
	1
	1

	TOTAL 
	 
	 


17.

	Motor Description: Ash water return (Big) motor: 587373


	Output 

Power (kW)485
	Voltage (V)

3.3 kV
	Current (A) 

105 A
	Speed (rpm)

1488
	Weight 

2.5 Ton


	No.
	Description
	 Estimated Quantity Rate 
	 Breakdown Rate 
	Total
	Estimated  Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	10
	3

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	10
	3

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	10
	3

	4
	Polish stator feet
	 
	 
	 
	10
	3

	5
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	10
	3

	6
	Overhaul rotor & spray with insulating varnish
	 
	 
	 
	10
	3

	7
	Supply DE and NDE "V" Seals
	 
	 
	 
	10
	3

	8
	Supply and fit DE bearings -NU 322
	 
	 
	 
	10
	3

	9
	Supply and fit NDE bearing - 6322
	 
	 
	 
	10
	3

	10
	Re-sleeve DE bearing housing
	 
	 
	 
	10
	3

	11
	Re-sleeve NDE bearing housing
	 
	 
	 
	10
	3

	12
	Supply and fit new terminal box and cover
	 
	 
	 
	3
	1

	13
	Supply and fit 1xheater box
	 
	 
	 
	3
	1

	14
	Supply new fan and fan cover
	 
	 
	 
	10
	3

	15
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	10
	3

	16
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	10
	3

	17
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	10
	3

	18
	Replace all grease pipes and fittings
	 
	 
	 
	10
	3

	19
	Reassemble motor
	 
	 
	 
	10
	3

	20
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test
	 
	 
	 
	10
	3

	21
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	10
	3

	22
	Fit the shaft locking device
	 
	 
	 
	10
	3

	23
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	10
	3

	
	 Rewind
	 
	 
	 
	 
	 

	24
	Rewind stator
	 
	 
	 
	5
	2

	25
	Re-bar rotor
	 
	 
	 
	2
	1

	26
	New stator core
	 
	 
	 
	1
	1

	TOTAL 
	 
	 


18. 

	Motor Description:Electric Mulsifier pump motor:141205
	Output 

Power (kW)261
	Voltage (V)

3.3 kV
	Current (A) 

45 A
	Speed (rpm)

1480
	Weight 

2 Ton


	No.
	Description
	 Rate 
	 Breakdown Rate 
	Total
	Estimated  Quantity
	Breakdown Quantity

	Basic overhaul

	1
	Collect motor from Kriel Power Station
	 
	 
	 
	5
	2

	2
	Dismantle, clean, test & assess all parts. Provide Kriel with a QCP. Tests should include, as a minimum: IR, PI, Winding Resistance, El-Cid, Bar to bar continuity, core flux test
	 
	 
	 
	5
	2

	3
	Perform Non-Destructive Testing on the rotor shaft and provide feedback on the condition of the motor.
	 
	 
	 
	5
	2

	4
	Polish stator feet
	 
	 
	 
	5
	2

	5
	Overhaul stator & spray with insulating varnish
	 
	 
	 
	5
	2

	6
	Overhaul rotor & spray with insulating varnish
	 
	 
	 
	5
	2

	7
	Supply DE and NDE "V" Seals
	 
	 
	 
	5
	2

	8
	Supply and fit DE bearings - NU220 EM1 C3 
	 
	 
	 
	5
	2

	9
	Supply and fit NDE bearing - 6220 C3
	 
	 
	 
	5
	2

	10
	Re-sleeve DE bearing housing
	 
	 
	 
	5
	2

	11
	Re-sleeve NDE bearing housing
	 
	 
	 
	5
	2

	12
	Overhaul & clean heat exchangers
	 
	 
	 
	5
	2

	13
	Supply and fit new terminal box and cover
	 
	 
	 
	2
	1

	14
	Supply and fit 1xheater box
	 
	 
	 
	2
	1

	15
	Supply new fan 
	 
	 
	 
	3
	1

	16
	Micro-weld and machine DE &NDE bearing journals
	 
	 
	 
	5
	2

	17
	Dynamically balance the rotor at operating speed according to ISO 1940/1 balancing grade G6.3 (Balancing certificate to be included in test report).
	 
	 
	 
	5
	2

	18
	Replace all the rubber seals and gaskets, including refurbishment of terminal boxes
	 
	 
	 
	5
	2

	19
	Replace all grease pipes and fittings
	 
	 
	 
	5
	2

	20
	Reassemble motor
	 
	 
	 
	5
	2

	21
	Test run the motors in the presence of an Eskom representative and submit a report. Motor to be at full Voltage (3.3kV) for the duration of the test.
	 
	 
	 
	5
	2

	22
	Paint the motors light grey (gloss enamel G29)
	 
	 
	 
	5
	2

	23
	Fit the shaft locking device
	 
	 
	 
	5
	2

	24
	Return the motor back to site (Kriel Power Station)
	 
	 
	 
	5
	2

	Rewind

	25
	Rewind stator
	 
	 
	 
	2
	1

	26
	Re-bar rotor
	 
	 
	 
	1
	1

	27
	New stator core
	 
	 
	 
	1
	1

	TOTAL 
	 
	 


	No
	Stock Number
	Bearings
	 Rate 
	Quantity
	Amount

	1
	34061
	BEARING, SLEEVE: TYPE: MILL MOTOR; INSIDE DIAMETER: 127 MM; OUTSIDE DIAMETER: 157 MM; LENGTH: 127 MM; MATERIAL: WHITE METAL; SIZE: 5; SUPPLIER NOTE: 
	 
	30
	 

	2
	251388
	BEARING, SLEEVE: TYPE: MILL MOTOR; INSIDE DIAMETER: 110 MM; MATERIAL: WHITE METAL; FOR USE ON 328 KW MOTOR; UNIT 1TO 3; NDE/DE;
	 
	30
	 

	3
	588610
	BEARING, SLEEVE: TYPE: JOURNAL; INSIDE DIAMETER: 140 MM;OUTSIDE DIAMETER: 274 MM; LENGTH: 105 MM; MATERIAL: WHITE METAL;APPLICATION: USED ON THE HORIZONTAL BEARING ASSEMBLY ON NEW U4-6 MILL MOTOR; DRAWING NO: BP11611; PART NO:HRS14/EARP140/SS160/SB140/I; VENDORS ARE RESPONSIBLE FOR ENSURING THAT THEY ARE PERFORMING AGAINST THE CORRECT DRAWING
	 
	30
	 

	4
	33554
	BEARING, SLEEVE: TYPE: PA FAN MOTOR; INSIDE DIAMETER: 114 MM; OUTSIDE DIAMETER: 155 MM; LENGTH: 127 MM; MATERIAL: WHITE METAL; SIZE: 4.5 IN; MOTOR JKD 400/6, 465 KW, 3,3 KV, LM2556/04,
	 
	25
	 

	5
	588609
	BEARING, SLEEVE: TYPE: JOURNAL; INSIDE DIAMETER: 100 MM; OUTSIDE DIAMETER: 209 MM; LENGTH: 80 MM; MATERIAL: WHITE METAL; SIZE: 4
	 
	20
	 

	6
	50748
	BEARING, SLEEVE: TYPE: JOURNAL; INSIDE DIAMETER: 250 MM; OUTSIDE DIAMETER: 325 MM; MATERIAL: WHITE METAL; SUPPL P/N: BS2613-1970
	 
	25
	 

	7
	251385
	BEARING, SLEEVE: INSIDE DIAMETER: 250 MM; MATERIAL: WHITE METAL; REFERENCE NO: DO 5032; FOR USE ON ELECTRIC PUMP MOTOR; NDE/DE;
	 
	25
	 

	8
	565476
	BEARING, SLEEVE: TYPE: EFP MOTOR; INSIDE DIAMETER: 250 MM; OUTSIDE DIAMETER: 428.84 MM; LENGTH: 205 MM; MATERIAL: GR 420/12; MAN
	 
	25
	 

	9
	714646
	BEARING, SLEEVE: TYPE: EXTERNAL OIL FEED SLIDE; INSIDE DIAMETER: 250 MM; OUTSIDE DIAMETER: 380 MM; LENGTH: 200 MM; MATERIAL: WHITE METAL; SPECIFICATION: ISO11687-3 DIN31694; SIZE: 22-250 MM; OEM P/N: EMZLB 22-250; CAT NO: RH- 1046;
	 
	25
	 

	10
	714637
	BEARING, SLEEVE: TYPE: EXTERNAL OIL FEED SLIDE NON-LOCATING; INSIDE DIAMETER: 250 MM; OUTSIDE DIAMETER: 380 MM; LENGTH: 200 MM; MATERIAL: WHITE METAL; SPECIFICATION: ISO11687-3 DIN31694; SIZE: 22-250 MM; OEM P/N: EMZLQ 22-250; CAT NO: RH-1046;
	 
	25
	 

	11
	251383
	BEARING, SLEEVE: TYPE: FD FAN MOTOR; INSIDE DIAMETER: 225 MM; OUTSIDE DIAMETER: 350 MM; LENGTH: 200 MM; MATERIAL: WHITE METAL; DRAWING NO: HSR22/EARP225/SS250.SB250/I REV 0; FOR USE ON 3050 KW MOTOR (SERIAL NO:DO 5027/01), NDE/DE; SIZE: 22 MM;
	 
	15
	 

	12
	694224
	BEARING, SLEEVE: TYPE: JOURNAL; INSIDE DIAMETER: 200 MM; OUTSIDE DIAMETER: 350 MM; LENGTH: 200 MM; MATERIAL: STL WHITE METAL LINED
	 
	15
	 

	13
	34056
	BEARING, SLEEVE: TYPE: JOURNAL; INSIDE DIAMETER: 200 MM; OUTSIDE DIAMETER: 408 MM; LENGTH: 210 MM; MATERIAL: STL WHITE METAL LINED; 
	 
	15
	 

	TOTAL 
	 


	TOTAL OF THE TOTALS
	 




DOCUMENT C2.1
PAGE 2
PRICING DATA




Part C2: Pricing Data
PAGE 1
C2 TSC3 Cover

