Eskom Holdings SOC Ltd

Contract number _____________
project and contract title: REFURBISHMENT OF MEDIUM VOLTAGE MOTORS, AS STOCK ITEMS ON AN “AS AND WHEN” REQUIRED BASIS FOR A PERIOD OF FIVE YEARS AT KRIEL POWER STATION, MAIN STORES.




Part 3: Scope of Work

	Document reference
	Title
	No of pages

	
	This cover page
	1

	C3.1
	Employer’s Service Information
	16

	C3.2
	Contractor’s Service Information

(insert at award stage or delete if not applicable)
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	Total number of pages
	17


C3.1: Employer’s service Information

Contents

1Part 3: Scope of Work

C3.1: Employer’s service Information
2
1
Description of the service
4
1.1
Executive overview
4
1.2
Employer’s requirements for the service
4
1.2.1
General Requirements Of The Works
4
1.2.2
Scope of work description
4
1.2.3
Assessment
5
1.2.4
Testing
5
1.2.5
Materials
5
1.2.6
Medium Voltage Motors to be refurbished.
5
1.2.7
List of MV motor bearings as stock items
7
1.3
Interpretation and terminology
7
2
Management strategy and start up.
9
2.1
The Contractor’s plan for the service
9
2.2
Management meetings
9
2.3
Contractor’s management, supervision and key people
9
2.4
Provision of bonds and guarantees
9
2.5
Documentation control
10
2.6
Invoicing and payment
10
2.7
Contract change management
10
2.8
Records of Defined Cost to be kept by the Contractor
10
2.9
Insurance provided by the Employer
10
2.10
Training workshops and technology transfer
10
2.11
Design and supply of Equipment
10
2.12
Things provided at the end of the service period for the Employer’s use
10
2.12.1
Equipment
10
2.12.2
Information and other things
11
2.13
Management of work done by Task Order
11
3
Health and safety, the environment and quality assurance
12
3.1
Health and safety risk management
12
3.2
Environmental constraints and management
12
3.3
Quality assurance requirements
12
4
Procurement
13
4.1
People
13
4.1.1
Minimum requirements of people employed
13
4.1.2
BBBEE and preferencing scheme
13
4.1.3
Accelerated Shared Growth Initiative – South Africa (ASGI-SA)
13
4.2
Subcontracting
13
4.2.1
Preferred subcontractors
13
4.2.2
Subcontract documentation, and assessment of subcontract tenders
14
4.2.3
Limitations on subcontracting
14
4.2.4
Attendance on subcontractors
14
4.3
Plant and Materials
14
4.3.1
Specifications
14
4.3.2
Correction of defects
14
4.3.3
Contractor’s procurement of Plant and Materials
14
4.3.4
Tests and inspections before delivery
14
4.3.5
Plant & Materials provided “free issue” by the Employer
14
4.3.6
Cataloguing requirements by the Contractor
14
5
Working on the Affected Property
15
5.1
Employer’s site entry and security control, permits, and site regulations
15
5.2
People restrictions, hours of work, conduct and records
15
5.3
Health and safety facilities on the Affected Property
15
5.4
Environmental controls, fauna & flora
15
5.5
Cooperating with and obtaining acceptance of Others
15
5.6
Records of Contractor’s Equipment
15
5.7
Equipment provided by the Employer
15
5.8
Site services and facilities
16
5.8.1
Provided by the Employer
16
5.8.2
Provided by the Contractor
16
5.9
Control of noise, dust, water and waste
16
5.10
Hook ups to existing works
16
5.11
Tests and inspections
16
5.11.1
Description of tests and inspections
16
5.11.2
Materials facilities and samples for tests and inspections
16
6
List of drawings
17
6.1
Drawings issued by the Employer
17


1 Description of the service
1.1 Executive overview 
Kriel Power Station experiences the need to repair and refurbish medium Voltage motors on a regular basis. This includes planned refurbishments as well as unplanned repairs which arise during breakdowns. The intent is to have a contract in place which will allow the repairs to be done on an “as and when” required basis.
1.2 Employer’s requirements for the service
1.2.1 General Requirements Of The Works
a) The works entails the following :

i) Collect, 
ii) Dismantle, 
iii) Assess, 
iv) Repair, 
v) Rewind, 
vi) Overhaul, 
vii) Assemble,
viii) Paint, 
ix) Test, 
x) Supply of spares, 
xi) Delivery, 
xii) Replacement of existing MV Motors  
b) All work performed should be in line with SANS 10242-1: 
c) The rewinding and refurbishing of rotating electrical machines Part 2: Medium-voltage three-phase induction motors. 
d) The motors are to be transported in line with 240-56361435 Transport of Power Station Electric Motors Standard. 
e) The stock items will be supplied as per description/specification given by Eskom Kriel power station and the acceptance of the spare it will be against the set specification. 
f) Any ambiguity on the supplied specification will be clarified before the procurement of the spare by the Contractor, failure to clarify will lead to the items not being accepted and not paid for by Eskom.

1.2.2 Scope of work description

a) All the motors are to be cleaned properly. Shot blasting is preferred (no sandblasting or chemical cleaning).

b) Removal of the windings is to be carried out strictly in accordance with SABS 0242-1 specifications.

c) Method of varnishing to be DD and baked or VPI, unless otherwise called for Actuator Duty Cycles; to be approximately 1500 starts per hour and recommended class H.

d) Paint work to be done as per SABS064 for the type of paint and the method of application.

e) After painting of the motors is completed, the shafts should be treated for rust prevention. (Shaft journals are to be micro welded or new shafts are to be provided, according to SABS 0242) Metal spraying of shafts is not accepted.

f) Two sets of Thermistors (i.e. 2 per phase = 6) are to be installed on all motors at all times where Thermistors were originally provided, and one set of Thermistors are to be installed on all actuator motors.

g) Terminal leads must be clearly marked and of a reasonable length to enable joints to be carried out.

1.2.3 Assessment

Collect from Kriel Power station, strip, and clean, electrical test (stator and rotor), assess mechanical components, investigate, and make proposals to prevent future re-occurrence as well as determining the scope of work.
1.2.4 Testing 
a) Eskom reserves the right to inspect the motors or associated parts at any stage of maintenance, and to witness routine and performance tests. All tests should be conducted in line with SANS 10242-1.

b) All motors are to be tested by the Contractor prior to delivery, and test results are approved by the Employer, based on meeting requirements. Eskom Quality Personnel, System Engineer, maintenance, and vibration’s analyst to witness the testing.

c) Test certificates are required for all tests performed.

d) Routine tests are performed on all repaired motors.

e) Special tests are performed when specified by the Employer.
1.2.5 Materials 
	Bearings
	Only SKF, FAG, RHP or NSK bearings are to be used.

	Lubrication
	Shell Alvania, R2 and R3

ENGEN Premium 3 

	Fans
	OEM unless otherwise specified.

	Heat exchanger
	OEM unless otherwise specified.

	Terminal boxes/blocks/connections
	OEM unless otherwise specified 


1.2.6 Medium Voltage Motors to be refurbished.
1. 

	Motor Description: 

Electric feed pump (EFP) motor: 141271
	Output 

Power (kW)

10 000
	Voltage (V)

11kV
	Current (A) 

601 A
	Speed (rpm)

1492
	Weight 

35 Ton


2. 

	Motor Description:

Forced Draught Fan (FD) motor: 141233
	Output 

Power (kW)

3050
	Voltage (V)

3.3 kV
	Current (A) 

636 A
	Speed (rpm)

741
	Weight 

20 Ton


3. 

	Motor Description:

Induced Draught Fan(ID)Motor: 141234
	Output 

Power (kW)

2500
	Voltage (V)

3.3 kV
	Current (A) 

538 A
	Speed (rpm)

597
	Weight 

20 Ton


4. 

	Motor Description:

PA fan (U1-3) Motor: 179099
	Output 

Power (kW)

465
	Voltage (V)

3.3 kV
	Current (A) 

98 A
	Speed (rpm)

1492
	Weight 

4.5 Ton


5. 

	Motor Description:

PA fan (U4-6) Motor: 179096
	Output 

Power (kW)

650
	Voltage (V)

3.3 kV
	Current (A) 

113 A
	Speed (rpm)

1488
	Weight 

5 Ton


6.

	Motor Description:

Mill (U1-3)

Motor: 141218
	Output 

Power (kW)

328
	Voltage (V)

3.3 kV
	Current (A) 

74 A
	Speed (rpm)

938
	Weight 

4.5 Ton


7. 

	Motor Description:

Mill (U4-6) Motor: 179095
	Output 

Power (kW)

570
	Voltage (V)

3.3 kV
	Current (A) 

130 A
	Speed (rpm)

986
	Weight 

5.5 Ton


8. 

	Motor Description:

Condensate Extraction Pump (CEP) motor: Vertical: 179098
	Output 

Power (kW)

1500
	Voltage (V)

3.3 kV
	Current (A) 

310 A
	Speed (rpm)

1488
	Weight 

6 Ton


9.

	Motor Description: Cooling water (CW) pump motor: vertical:179097
	Output 

Power (kW)

1500
	Voltage (V)

3.3 kV
	Current (A) 

340 A
	Speed (rpm)

330
	Weight 

20 Ton


10.

	Motor Description:

Ash pump motor: 217674

	Output 

Power (kW)

420
	Voltage (V)

3.3 kV
	Current (A) 

87 A
	Speed (rpm)

1481
	Weight 

3 Ton


11. 

	Motor Description:

Sluice pump motor: 141279
	Output 

Power (kW)

300
	Voltage (V)

3.3 kV
	Current (A) 

63 A
	Speed (rpm)

1477
	Weight 

3 Ton


12.

	Motor Description:

Centac Compressor motor: 501009
	Output 

Power (kW)

530
	Voltage (V)

3.3 kV
	Current (A) 

109 A
	Speed (rpm)

2969
	Weight 

3 Ton


13.

	Motor Description:

Demag Compressor motor: 500980

	Output 

Power (kW)

650
	Voltage (V)

3.3 kV
	Current (A) 

136 A
	Speed (rpm)

2955
	Weight 

3.5 Ton


14.

	Motor Description:

Cameron Compressor motor: 664141
	Output 

Power (kW)

510
	Voltage (V)

3.3 kV
	Current (A) 

102 A
	Speed (rpm)

2969
	Weight 

3 Ton


15.

	Motor Description:

HP Demin motor: 614532
	Output 

Power (kW)

160
	Voltage (V)

3.3 kV
	Current (A) 

36 A
	Speed (rpm)

1484
	Weight 

2 Ton


16.

	Motor Description:

Ash water return (small) motor: 141329

	Output 

Power (kW)

300
	Voltage (V)

3.3 kV
	Current (A) 

55 A
	Speed (rpm)

1484
	Weight 

2.5 Ton


17.

	Motor Description:

Ash water return (Big) motor: 587373

	Output 

Power (kW)

485
	Voltage (V)

3.3 kV
	Current (A) 

105 A
	Speed (rpm)

1488
	Weight 

2.5 Ton


18. 

	Motor Description:

Electric Mulsifier pump motor: 141205
	Output 

Power (kW)

261
	Voltage (V)

3.3 kV
	Current (A) 

45 A
	Speed (rpm)

1480
	Weight 

2 Ton


1.2.7  List of MV motor bearings as stock items

The service provider must be able to provide technical support relating to MV motor bearings (including coming to site) and also to supply and deliver new bearings to Kriel power station.

Please note: Where applicable Kriel Power Station will free issue the new bearing to the supplier whereby the supplier will not cost Kriel Power Station for the new bearing issued.
	
	Bearings
	Stock Number
	Quantity

	1
	BEARING, SLEEVE: TYPE: MILL MOTOR; INSIDE DIAMETER: 127 MM; OUTSIDE DIAMETER: 157 MM; LENGTH: 127 MM; MATERIAL: WHITE METAL; SIZE: 5; SUPPLIER NOTE: 
	34061
	30

	2
	BEARING, SLEEVE: TYPE: MILL MOTOR; INSIDE DIAMETER: 110 MM; MATERIAL: WHITE METAL; FOR USE ON 328 KW MOTOR; UNIT 1TO 3; NDE/DE;
	251388
	30

	3
	BEARING, SLEEVE: TYPE: JOURNAL; INSIDE DIAMETER: 140 MM;OUTSIDE DIAMETER: 274 MM; LENGTH: 105 MM; MATERIAL: WHITE METAL;APPLICATION: USED ON THE HORIZONTAL BEARING ASSEMBLY ON NEW U4-6 MILL MOTOR; DRAWING NO: BP11611; PART NO:HRS14/EARP140/SS160/SB140/I; VENDORS ARE RESPONSIBLE FOR ENSURING THAT THEY ARE PERFORMING AGAINST THE CORRECT DRAWING
	588610
	30

	4
	BEARING, SLEEVE: TYPE: PA FAN MOTOR; INSIDE DIAMETER: 114 MM; OUTSIDE DIAMETER: 155 MM; LENGTH: 127 MM; MATERIAL: WHITE METAL; SIZE: 4.5 IN; MOTOR JKD 400/6, 465 KW, 3,3 KV, LM2556/04,
	33554
	25

	5
	BEARING, SLEEVE: TYPE: JOURNAL; INSIDE DIAMETER: 100 MM; OUTSIDE DIAMETER: 209 MM; LENGTH: 80 MM; MATERIAL: WHITE METAL; SIZE: 4
	588609
	20

	6
	BEARING, SLEEVE: TYPE: JOURNAL; INSIDE DIAMETER: 250 MM; OUTSIDE DIAMETER: 325 MM; MATERIAL: WHITE METAL; SUPPL P/N: BS2613-1970
	50748
	25

	7
	BEARING, SLEEVE: INSIDE DIAMETER: 250 MM; MATERIAL: WHITE METAL; REFERENCE NO: DO 5032; FOR USE ON ELECTRIC PUMP MOTOR; NDE/DE;
	251385
	25

	8
	BEARING, SLEEVE: TYPE: EFP MOTOR; INSIDE DIAMETER: 250 MM; OUTSIDE DIAMETER: 428.84 MM; LENGTH: 205 MM; MATERIAL: GR 420/12; MAN
	565476
	25

	9
	BEARING, SLEEVE: TYPE: EXTERNAL OIL FEED SLIDE; INSIDE DIAMETER: 250 MM; OUTSIDE DIAMETER: 380 MM; LENGTH: 200 MM; MATERIAL: WHITE METAL; SPECIFICATION: ISO11687-3 DIN31694; SIZE: 22-250 MM; OEM P/N: EMZLB 22-250; CAT NO: RH- 1046;
	0714646
	25

	10
	BEARING, SLEEVE: TYPE: EXTERNAL OIL FEED SLIDE NON-LOCATING; INSIDE DIAMETER: 250 MM; OUTSIDE DIAMETER: 380 MM; LENGTH: 200 MM; MATERIAL: WHITE METAL; SPECIFICATION: ISO11687-3 DIN31694; SIZE: 22-250 MM; OEM P/N: EMZLQ 22-250; CAT NO: RH-1046;
	0714637
	25

	11
	BEARING, SLEEVE: TYPE: FD FAN MOTOR; INSIDE DIAMETER: 225 MM; OUTSIDE DIAMETER: 350 MM; LENGTH: 200 MM; MATERIAL: WHITE METAL; DRAWING NO: HSR22/EARP225/SS250.SB250/I REV 0; FOR USE ON 3050 KW MOTOR (SERIAL NO:DO 5027/01), NDE/DE; SIZE: 22 MM;
	251383
	15

	12
	BEARING, SLEEVE: TYPE: JOURNAL; INSIDE DIAMETER: 200 MM; OUTSIDE DIAMETER: 350 MM; LENGTH: 200 MM; MATERIAL: STL WHITE METAL LINED
	694224
	15

	13
	BEARING, SLEEVE: TYPE: JOURNAL; INSIDE DIAMETER: 200 MM; OUTSIDE DIAMETER: 408 MM; LENGTH: 210 MM; MATERIAL: STL WHITE METAL LINED; 
	34056
	15


1.3 Interpretation and terminology
The following abbreviations are used in this Service Information:

	Abbreviation
	Meaning given to the abbreviation

	OBL
	Outside battery limits

	
	


2 Management strategy and start up.
2.1 The Contractor’s plan for the service
The Contractor shall submit a plan to the Service Manager for acceptance within the period stated in the Part C1.2a Data by Employer of Part C1 agreements and contract data. 

2.2 Management meetings
All relevant meetings must be attended.

Regular meetings of a general nature may be convened and chaired by the Supply Manager as follows:

	Title and purpose
	Approximate time & interval
	Location
	Attendance by:

	Risk register and compensation events
	Quarterly 
	Kriel PS
	Employer, Contractor, and Service Manager

	Overall contract progress and feedback
	Quarterly
	Kriel PS
	Employer, Contractor, and Service Manager

	
	
	
	

	
	
	
	


Meetings of a specialist nature may be convened as specified elsewhere in this Service Information or if not so specified by persons and at times and locations to suit the Parties, the nature and the progress of the service.  Records of these meetings shall be submitted to the Service Manager by the person convening the meeting within five days of the meeting.  
All meetings shall be recorded using minutes or a register prepared and circulated by the person who convened the meeting.   Such minutes or register shall not be used for the purpose of confirming actions or instructions under the contract as these shall be done separately by the person identified in the conditions of contract to carry out such actions or instructions.  

2.3 Contractor’s management, supervision and key people

a) The Contractor to provide a key list of personnel who will carry out the work on site with their qualifications attached. 

b) A company organogram shall be shared with the Service Manager to communicate accordingly to comply with the NEC3 Term Services Contract communication structures. 

c) The Contractor shall provide a site manager/contract manager to manage all contract related matters.  Such persons is preferred to have prior experience in contract management and change of this person is communicated in writing, within 1 (one) week of such change, to the Employer.
d) The Contractor’s supervisor shall be knowledgeable, competent and fully capable to perform supervisory duties without direct or continuous supervision by the employer, to liaise and co-ordinate activities with various departments, including the employer’s personnel and others in order to fulfill all obligations.  

e) In the absence of the relevant Site Manager or Supervisor, a replacement must be identified to take over the duties.
2.4 Provision of bonds and guarantees

Not applicable to this contract
2.5 Documentation control

a) The information for spares to shared electronically or hard copy.

b) Other information provided with each spare to be shared electronic or hard copy.

c) Information provided to be documented in such a manner that the information for each spare will be easily identifiable. 

2.6 Invoicing and payment
Within one week of receiving a payment certificate from the Service Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice showing the amount due for payment equal to that stated in the Service Manager’s payment certificate.  
The Contractor shall address the tax invoice to Invoiceseskomlocal@eskom.co.za
and include on each invoice the following information:

· Name and address of the Contractor and the Service Manager; 

· The contract number and title;

· Contractor’s VAT registration number;

· The Employer’s VAT registration number 4740101508;
· Description of service provided for each item invoiced based on the Price List;
· Total amount invoiced excluding VAT, the VAT and the invoiced amount including VAT;
· Purchase order number 
· GR Number 
· Contractor shall invoice after approval of Assessment, Payment certificate and GR 

2.7 Contract change management 
a) Any change of the Contractor’s company ownership should be communicated through to the Service Manager. Failing to do this may lead to contract termination with legal consequences. 

b) The correct processes and procedures will be communicated through to the Contractor by the Service Manager.

c) If the Employer’s Service Manager change the Contractor will be notified by the Employer as soon as possible to ensure that the Contractor follow the correct communication channels.

2.8 Records of Defined Cost to be kept by the Contractor
To substantiate the Defined Cost of Compensation Events, the Contractor shall keep records of amounts paid.
2.9 Insurance provided by the Employer
As stated in Contract Data and as per Table A within this Service Agreement
2.10 Training workshops and technology transfer

Not applicable to this contract
2.11 Design and supply of Equipment
The Contractor submits a service report at the end of work which details all activities performed deviation and noted defects which could not be fixed in the allocated time. This report will also be accompanied by a handover certificate which the Employer must sign to declare that all activities have been done as per scope of work.
2.12 Things provided at the end of the service period for the Employer’s use
2.12.1 Equipment
The Contractor shall hand over a serviceable plant to the Employer by the end of this contract.
2.12.2 Information and other things
a) At the end of the service period the Contractor returns all Equipment and surplus materials to the Employer.
b) Provides items of equipment for the Employer’s use as stated in the Service Information and provides information and other things as stated in the Service Information.
2.13 Management of work done by Task Order
a) A Task is work within the service which the Service Manger may instruct the Contractor to carry out within a stated period.  

b)
A signed Task Order is the Service Manager’s instruction to carry out a Task.

c) Task Completion is when the Contractor has done all the work in the Task and corrected Defects which would have prevented the Employer or Others from using the Affected Property and Others from doing their work.

d) Task Completion Date is the date for completion stated in the Task Order unless later changed in accordance with this contract.

e)
A Task Order includes:

-     A detailed description of the work in the Task

-     A priced list of items of work in the Task in which items taken from the Price List are identified.

-     The starting and completion dates for the Task

-     Conditions of the service agreement is in accordance with the Task Order issued

f) The Service Manager consults the Contractor about the contents of a Task Order before he issues it.

g) The Prices for items in the Task price list which are not taken from the Price List are assessed in the same way as compensation events.

h)
No Task Order is issued after the end of the service period.

i) Work will not commence on site without the Contractor receiving a signed detailed task order that has been agreed upon by the Service Manager and the Contractor.

j) It is the Contractor’s responsibility to provide the Service Manager a detailed Task Order programme for acceptance within the period stated in the Contract Data.

k) Only when the Task Order programme is accepted and agreed upon by the Service Manager and the Contractor will any work commence on site.

l) When any emergencies do arise, it is required from the Contractor to adhere to the following terms:

· The Contractor will be informed of emergencies when the Service Manager first becomes aware of it. 

      -      Response time within 2 hours for any communication when the Contractor acknowledges the 

             emergency.

      -      Provide a programme within 8 hours after Task Order provided to the Contractor.
      -      Mobilise within 5 hours after Task Order have been accepted by both parties.
3 Health and safety, the environment and quality assurance
3.1 Health and safety risk management

a) The Contractor shall comply with Section 10 of Occupational Health and Safety Act (Act No.85 of 1993) when manufacturing any goods for this contract.

b) The Contractor shall comply with site health and safety requirements for Kriel Power Station when delivering goods.

c) Site delivery safety requirements to be adhered to - And can be obtained through the Purchaser’s.

             Manager In line with the SHE specification

d) The Contractor shall submits safety file for approval before access is granted.

e) The Contractor shall maintains the safety file validity in line with site requirements.

f)     The mode of transport for delivery should comply with site requirement in line with issued SHE

             specification
3.2 Environmental constraints and management

a) The vehicle used for Delivery; by ensuring that there are no oil spillages, and the vehicle emission is not emitting beyond limits. 

b) The Material used for supporting the goods being delivered are correctly disposed and are without harm to environment. 

c) The Contractor shall comply with Site Environmental management plan (EMP) and other requirement.

d) The Contractor shall comply with Environmental aspect and impact register.

e) The Contractor shall comply with all Site’s environmental management procedures, especially the waste management and oil spillages.

3.3 Quality assurance requirements

a) The Contractor shall compiles the baseline Quality Control plan.

b) Quality Control Plan (QCP) must be approved by both the Contractor, Eskom engineer and QC inspector before commencing with any deliveries at the beginning of the Contract.

c) Material certificates, mechanical testing certificate and NDT certificates should be part of the data package accompanying the QCPs.

d) All delivered goods will be subjected to QC verification by an Employer’s Quality personnel at receiving as per detailed item description found in heading 2 table.

e) The Contractor shall comply with Eskom’s Supply Quality Management Specification (Document No: 240-105658000) and ISO 9001:2015 requirements.

f)    The Employer will on frequent basis conduct the Contractor’s performance/ compliance in accordance to QM 58 and ISO 9001 and NCR will be raised for non-compliance.

4 Procurement
4.1 People
4.1.1 Minimum requirements of people employed
It is the Contractor’s sole responsibility to ensure all its employees have permits to perform work in the Republic of South Africa.
4.1.2 BBBEE and preferencing scheme

a) Where a change in the Contractor’s legal status, ownership or any other change to his business composition or business dealings results in a change to the Contractor’s B-BBEE status, the Contractor notifies the Employer within seven days of the change.

b) The Contractor is required to submit an updated verification certificate and necessary supporting documentation confirming the change in his B-BBEE status to the Employer within thirty days of the notification or as otherwise instructed by the Employer.

c) Where, as a result, the Contractor’s B-BBEE status has decreased since the starting date the Employer may either re-negotiate this contract or alternatively, terminate the Contractor’s obligation to provide the service.

d) Failure by the Contractor to notify the Employer of a change in its B-BBEE status may constitute a reason for termination will be dealt with according to the NEC3 TSC penalty/termination clauses
4.1.3 Accelerated Shared Growth Initiative – South Africa (ASGI-SA) 

Not Applicable
4.2 Subcontracting
4.2.1 Preferred subcontractors
Subcontractors can be used following the Project Manager’s acceptance to any of the below:

-
EME or QSE entities at least 51% owned by Black Youth Owned;

-
EME or QSE entities at least 51% owned by Black People with Disability.

-
EME or QSE entities at least 51% owned by Black People;

-
EME or QSE entities at least 51% owned by Black Women

-
EME or QSE entities at least 51% owned by Black People with Disabilities

The following sub-contractor will be utilized in terms of this contract. The sub-contracting  percentage will not be a standard price therefore it will depend on the unit to be delivered

	Name of Sub-Contractor
	

	B-BBEE Level
	

	CSD number
	

	Scope
	

	Address
	


4.2.2 Subcontract documentation, and assessment of subcontract tenders

a) When the Contractor uses a Subcontractor, he needs to engage with him on a NEC basis. 

b) The Subcontractor needs adhere to all processes, policies and procedures of Eskom as service should be provided as if not subcontracted to Eskom.

c) All reporting will happen based on the NEC standard forms or as agreed upon in the Kick off meeting

4.2.3 Limitations on subcontracting

a) Appointment and managing the sub-contractor is the full responsibility of the Principal Contractor.

b) The Contractor does not subcontract the whole of the service.
c) The Contractor subcontracts only in accordance with this contract.
4.2.4 Attendance on subcontractors

a) The Subcontractor shall attend all morning feedback Outage meetings to provide accurate feedback on the progress of service. 

b) Assessment meetings between Service Manager and the Contractor should be avoided by the Subcontractor.

4.2.5 SDL&I Requirements
The following reflects the agreed Supplier Development, Localisation and Industrialisation (SDL&I) commitments between the Contractor and the Employer:

a) The Contractor shall allocate an amount equivalent to two percent (2%) of the total Contract Expenditure by Eskom towards the implementation of Community Social Investment (CSI) initiatives.
4.3 Plant and Materials

4.3.1 Specifications
Refer to Employer’s Service information 1.2 of Part C3 Scope of Work
4.3.2 Correction of defects
a) The Service Manager arranges with the Employer to allow the Contractor access if it is needed for correcting a Defect.

b) The Contractor needs to correct a Defect within one day or when the first available opportunity arises.
4.3.3 Contractor’s procurement of Plant and Materials

a) The Contractor will do all procurement of materials required to execute the service according to own procurement processes. 
b) All materials purchased by the Contractor to be installed to Affected Property will be kept and preserved according to the storage relevant specification. 
4.3.4 Tests and inspections before delivery

a) The Contractor does not utilise those Plant and Materials which the Service Information states are to be tested or inspected before delivery until the Service Manager has notified the Contractor that they have passes the test or inspection.
b) All holding points on QCP should have been adhered to and signed off by both parties before accepting any material or goods on site.
4.3.5 Plant & Materials provided “free issue” by the Employer
The Employer shall provide loading and offloading plant .
a) Forklift

b) Overhead crane
4.3.6 Cataloguing requirements by the Contractor
Not applicable to this contract
5 Working on the Affected Property
5.1 Employer’s site entry and security control, permits, and site regulations
a) The Contractor provides the necessary resources to carry out the service as stated in the Service Information.
b) The Contractor provides everything to carry out the Service Information of this contract unless where otherwise stated in this Service Agreement. Everything that should be provided by the Employer is stated in this Service Agreement, anything not stated in the Service Agreement should be provided by the Contractor to execute the work as stated in the Service Information.

5.2 People restrictions, hours of work, conduct and records
a) The Contractor shall provide the necessary resources to carry out the service as stated in the Service Information.
b) The Contractor shall provide everything to carry out the Service Information of this contract unless where otherwise stated in this Service Agreement. Everything that should be provided by the Employer is stated in this Service Agreement, anything not stated in the Service Agreement should be provided by the Contractor to execute the work as stated in the Service Information.
c) It is very important that the Contractor keeps records of his people working on the Affected Property, including those of his Subcontractors.
d) The Service Manager shall have access to all records of the Contractor and Subcontractor at any time when deemed necessary.
5.3 Health and safety facilities on the Affected Property
Any emergency equipment or fire suppression systems to be utilized by the Contractor when an emergency arise.
5.4 Environmental controls, fauna & flora

General environmental requirements referred to in section 3 above, Kriel Power Station ISO14001.
5.5 Cooperating with and obtaining acceptance of Others

a) The Contractor cooperates with the personnel during the service delivery. 
b) The Contractor cooperates with the Employer’s team during site visits and in ensuring that the service is delivered in accordance to all requirements.
5.6 Records of Contractor’s Equipment

a) The Contractor shall keep record of his equipment on site with relevant inspections carried out.
b) Inspection reports should be accessible by the Service Manager at any given time when he deems necessary. 

c) All equipment or tools signed in by the Contractor shall strictly adhere to the gate access rules and procedures.

d) All Equipment including hired shall be inspected and approved before accepted on site. 

e) The Contractor shall keep records of all hired Equipment to execute the Service Information
5.7 Equipment provided by the Employer
The Employer shall provide loading and off-loading Equipment when required by the Contractor.
a) Forklift

b) Overheads crane
5.8 Site services and facilities
5.8.1 Provided by the Employer
The Employer will provide in the way of water, waste disposal, ablutions, fire protection and lighting (etc) on the Affected Property. Power will be provided by the Employer the Contractor needs to ensure his own cabling, connections, DB Boards and CoC certificates of installations and connections.
a) Refuse Disposal
i) The Employer provides special colour coded bins for refuse disposal.These bins are emptied by the Employer free of charge.

ii) The Contractor ensures that all workers under his control strictly adhere to the correct use of refuse bins as stated in the Plant.

b) Supply of Electricity
i) Employer will make available to the Contractor 220/230-volt electrical supply free of charge from the closest existing point of supply. 

ii) The Contractor is to make provision for the necessary extensions and plug points.

iii) All Electrical boards must be inspected and tested before connecting to a power supply and then a CoC must be issued by the Contractor. 

iv) The Contractor will adhere to the Electrical Installation Regulations of 1992

c) Medical Facilities
i) The Contractor provides a First Aid service to his employees and subcontractor.  In the case where these prove to be inadequate, like in the event of a serious injury, the Employer’s Medical Centre and facilities are available.

ii) Outside the Employer’s office hours, the Employer’s First Aid Services are only available for serious injuries and life-threatening situations.

iii) The Employer is entitled, however, to recover the costs incurred, in the use of the above Employer’s facilities, from the Contractor.
d) Toilet Facilities
i) The Employer provides the Contractor access to toilet facilities.  

ii) Temporary chemical toilets are provided by the Contractor where deemed necessary.
5.8.2 Provided by the Contractor
Not applicable to this contract
5.9 Control of noise, dust, water and waste 

a) All necessary and relevant PPE shall be used at all times when entering site.
b) Risk assessments shall be completed before commencing with any task to be current at all times.

5.10 Hook ups to existing works

Any work performed at heights, Contractor must adhere to the correct safety standards, procedures and specifications stated in the health and safety risk management of Kriel Power Station.
5.11 Tests and inspections
5.11.1 Description of tests and inspections
As per the Employer’s service information 1.2 of Part C3 Scope of work
5.11.2 Materials facilities and samples for tests and inspections 
As per the Employer’s service information 1.2 of Part C3 Scope of work

6 List of drawings

6.1 Drawings issued by the Employer
Not applicable to this contract


Part C3: Scope of Work
1
C3 tsc3 Cover page

