## Slide 1: Renewable Hydrogen Facility: Clarification Meeting
June 2026

## Slide 2: Content
To engineer, procure and construct a water electrolysis hydrogen generation plant, which must be integrated with the existing renewable power plant for “Green H2 Production” at ERIC Rosherville
Location
Scope – Functional
Scope – Contractors
Tender Evaluation
Tips for Submission

## Slide 3
RHF
400 KW PV Plant
2.2 MWh BESS
NW Substation

## Slide 4: Scope - Functional
Electrolyser Technology:
Proton Exchange Membrane (PEM) or Anion Exchange Membrane (AEM)
Pressurised Alkaline Electrolyser
Operational Spec’s
Maximum power 50 - 65kW
Hydrogen Production: 24 kg / day
Hydrogen Purity: 99.9% purity
System Pressure: 27 Bar
Maximum Storage 80m3
Operational and Monitoring Requirements:
Operate on variable load
Monitoring for research

## Slide 5: Scope – Contractors Scope
Oxygen is vented
Control Room
Electrolyser(s): Upper total limit 65 kW (output of approximately. 24kg/day)
Electrolyser in container
Hydrogen Storage Tanks
3 x 24 m3 at electrolyser operating pressure
End-use container with Tap in Points
Potable water for operations
NW substation Electrical Connection
Water supply for Fire System
Demin water plant for electrolyser
Dryer for electrolyser
2.2MW BESS
400kW Solar Plant
Contractors Scope
Eskom to supply
Fire Detection system
H2 end use application off site
Gas Line
Single unit supplied by electrolyser manufacturer
400kW Solar Plant
2.2MW BESS
Electricity
Water
C&I
Remote Monitoring of operational conditions
Utility / Generator

## Slide 6: Tender Document
Scope:
Annexure A_Technical Specification for Renewable Hydrogen Facility
Annexure B_240-56227413 Hydrogen System Standard
Tender Evaluation:
20260407 Mandatory Technical Evaluation Criteria for RHF
20260407 Qualitative Technical Evaluation Criteria for RHF
240-RT&D-782 Technical Schedule for RHF (Documents to be completed and submitted with other technical returnable)
20260417 Tender Returnable Technical Schedule
Costing:
Renewable Hydrogen Facility – Typical Activity Schedule 05052026 (To be used as a guide when developing contractors activity schedule
NEC:
CI I ECC3_Hydrogen Facility_05052026 Final

## Slide 7: Tender Evaluation: Mandatory Criteria
Ref | Mandatory Technical Criteria Description | Motivation for use of Criteria
M1 | The electrolyser, including balance of plant, must be supplied by the Original Equipment Manufacturers (OEMs) or official local South African value adding reseller (VAR) or agents. The contractual agreement between the Tenderer and OEM must be provided. This could involve an agreement through a third party such as a local South African based value adding reseller (VAR) or agent. The contractual agreement between tenderer and OEM, must provide details showing: Which party is responsible for: supply, test, install, commission, maintain, modify, and conduct operating and maintenance training to the end user of the equipment. Should this responsibility be with the tenderer or local agent, the OEM shall confirm on a signed letter head that the local agent is authorized or accredited to perform these activities. The terms and duration of the agreements should match the contract duration of the RHF plant (as a minimum). The following will be accepted as proof of a contractual agreement: Declaration from both partied that an agreement is in place or the signature page of the agreement. In both cases the details of what is covered in the agreement must be provided. (non-binding letter of intent will not be considered as a contractual agreement) | Authorised plant equipment is installed, and guarantees can be upheld. Guarantee of the plant operation and support from the OEM and the local Agent. Confirm existing relationship between EPC (contractor) and OEM of electrolyser (manufacturer).
M2 | The contractor is required to submit a Deviation Schedule, (this is in addition to the 240-RT&D-782 Technical Schedule for Renewable Hydrogen Facility as required by 2.1 of the Qualitative Technical Evaluation Criteria). The Deviation Schedule must highlight deviation from all documents including NEC, VDSS, and any of the Eskom Standards as provided with the tender. This document will become a contractual document, should the tenderer be successful. | To ensure that the contractor is well informed on the expectation of the contract as well as supporting standards and guidelines to be used. To mitigate the possibility of contractors declaring compliance and unable to deliver on execution

## Slide 8: Tender Evaluation: Qualitative Criteria
The minimum weighted final score (threshold) required for a tender to be considered from a technical perspective is 80%. In addition, Criteria 2.1 and 2.2 have a criteria threshold of 80%. I.e. A score of 80% for Evaluation Criteria 2.1 and 2.2 must be achieved as well as an overall weighted score of 80% in order to pass the technical evaluation. (If the final weighted score is above 80% but the tenderer scores below 80% on Evaluation criteria 2.1 or 2.2, the tenderer will fail)
No. | Criteria | Weight
1 | General - Company Profile and Experience | 20 %
2 | Functional and operational Specification of major plant and equipment. | 25 %
3 | Mechanical Specifications | 10 %
4 | Control and Instrumentation | 10 %
5 | Electrical | 10 %
6 | Civil | 10 %
7 | Fire Protection | 10 %
8 | Quality Assurance | 5 %

## Slide 9: Company Profile and Experience (20%)
Ref | Criteria | Wt.
1.1 | 1.1.1. The Company Profile, Core Business Expertise and list of Experience will be evaluated to ensure that: The tenderer has 5 years’ experience or has completed 5 or more EPC contracts. 1.1.2. Reference Letter, Testimonials or Completion Certificates for completed hydrogen generations and balance of plant (BoP) projects will be evaluated to ensure that: The tenderer has demonstrated that they have designed, constructed and commissioned a full hydrogen plant. That this plant has been in operation for a period of more than three years from the date of commissioning without a significant failure? Eg cell stack 1.1.3 Contactable references must be provided. Project details with name of company and location, project description, size of electrolyser, contract value, construction period and operations performance of the plant. Should the tenderer choose to subcontract section of the scope this needs to be clearly stated. The company profile and work experience of the subcontractor must be submitted. The subcontractor will be evaluated on their experience based on the section of the scope they will be executing. | 30
1.2 | Evaluation of the CV’s will be to ensure that qualified personnel with the relevant experience are included during the design, construction, commissioning, and operation of the plant. The CV’s must show 5 years related experience and projects executed while performing at the level required by the scope (i.e 5 years’ experience as a lead discipline engineer), work performed on H2 generation and balance of plant (BoP), relevant qualifications (certified copies of certificate to be provided) and registration statue where relevant. The following CV’s must be provided as a minimum Engineering Work Design Lead (who has designed a hydrogen plant or has experience on hazardous works installation), Expert on Hydrogen plant and BoP design, installation, commissioning and integration, Mechanical Engineer, Electrical Engineer, C&I engineer, Civil Engineer, Person responsible for issuing the CoC for H2 installations, Master Installation Electrician | 40
1.3 | 1.3.1 Project Execution Plan will be evaluated to ensure that: The project scope if fully understood by the EPC contractor. Recourse have been assessed and are available for the execution of the project. Preliminary risks have been identified. 1.3.2 Project Program / Schedule will be evaluated to ensure that: Key milestones have been identified, and project timelines have been assessed, and are comparable with the Eskom timeline for project delivery. | 30

## Slide 10: Functional and operational Specification of major plant and equipment (25%)
Ref | Criteria | Wt.
2.1 | Level of compliance to the 240-RT&D-151 Specification for Renewable Hydrogen Facility and 240-56227413 Eskom Hydrogen System Standard will be assessed based on design information submitted (including but not limited to data sheet, drawings, P&IDs, control philosophy and maintenance manuals) to prove compliance to the Eskom standard for Hydrogen systems and on the completed 240-RT&D-782 Technical Schedule for Renewable Hydrogen Facility. | 25
2.2 | All technical data sheet, drawings, P&IDs, control philosophy and detailed maintenance manuals of the electrolyser and information provided from the OEM on the electrolyser will be evaluated to assess if the following functional specification are met: Electrolyser Technology to be supplied: Proton Exchange Membrane (PEM) or Anion Exchange Membrane (AEM) water electrolysis technology (preferred). Pressurised Alkaline Electrolyser (alternative) Plant operational parameters of 50kW – 65kW, 99.9% H2 purity, and production pressure of 27 bar. Capability and control philosophy for load following provided, with the ability to exceed the specified turndown ratio during testing Cell-stack life expectancy of >8 years. Minimum mean time between failures on cell stack. Warranty of 2 years on the cell stack and balance of plant. | 25
2.3 | Operational experience of the plant must be supplied by the tenderer. This will be evaluated to confirm that: Reference plant is of a similar size and application (industrial application) to the scope of work The plant has been in operation for a minimum of 3 years. (operation hour must equate to 3 years in service, approximately 18 000 hour) The tenderer has provided a contactable reference employed at an operational plant clearly indicating plant location, date of construction and commissioning. | 15
2.4 | The tenderer is to supply detail of the local agent which will be evaluated to ensure that the following criteria are met: the local agent or VAR has personnel in SA that are trained and able to offer technical support, fault finding, routine maintenance and supply spares OEM / authorised Local South African agent has a response time to rectify plant failure of < 21 days Direct communication channel between the end-user and OEM for technical support are possible (and facilitated by the contractor.) The OEM’s visits South Africa regularly to audit end-user satisfaction with Local Agent. | 15
2.5 | All technical data sheets, specification, OEM data, designs and drawing for other key component will be evaluated to determined compliance to the technical specification. This evaluation will be done on a component level for: H2 Electrolyser balance of plant (heaters, dryers, etc), Demineralising water treatment plant, H2 storage tanks, H2 end use station. | 10
2.6 | To ensure that the tenderers are certified to work on Hazardous Locations. The following must be provided: A letter or a certificate confirming that the company is certified to work on Hazardous Locations with Ex. Rated equipment received AND The letter or certificate confirming that the company is certified to work on a H2 plant | 10

## Slide 11: Mechanical Specifications (10%)
Ref | Criteria | Wt.
3.1 | The method statement and deviation schedule together with design detail (technical data sheets, drawings, P&IDs etc.), will be assessed to ensure that the hydrogen generating plant meets the requirements listed in the standards and specifications. | 40
3.2 | The CV of the Lead Discipline Engineer or Technologist (or other CVs of key personnel within the Mechanical Engineering field who are involved during the design, construction or commissioning phase of the project) will be evaluated to ensure a minimum of 5 years’ experience and professional registrations with the respective Governing bodies (such as ECSA or Equivalent). CV of key personnel proving hydrogen generating plant and BoP, design, installation and commissioning experience and capability etc., | 40
3.3 | Maintenance strategy and spares | 20

## Slide 12: Control and Instrumentation (10%)
Ref | Criteria | Wt.
4.1 | The contractor provides a high level C&I architecture drawing, clearly showing all interfaces and the different Ex zones. The architectural drawing as a minimum shows the following: Interface with electrical systems Interface with the existing PV plant Interface with the existing fire detection system (FDS) Third party interface through the Eskom IT network | 40
4.2 | The Tenderer must provide a minimum of three contactable reference plants where the proposed SCADA solution has been implemented. This can be presented in a table indicating plant name, commissioning date and SCADA used. The plants should be contactable and SCADA availability figures must be provided. The SCADA software and support (in terms of updates) must also be included. | 40
4.3 | The contractor provides all datasheets for the equipment that forms part of the C&I works. This includes but is not limited to field equipment, SCADA (All components forming the SCADA system), and HMI (All Components forming the human machine interface). | 20

## Slide 13: Electrical (10%)
Ref | Criteria | Wt.
5.1 | Level of compliance to 240-RT&D-151 Specification for Renewable Hydrogen Facility will be assessed in terms of the details provided by the contractor on 240-RT&D-782 Technical Schedule for Renewable Hydrogen Facility, Schedule F and the method statement. | 100

## Slide 14: Civil (10%)
Ref | Criteria | Wt.
6.1 | Provide a detailed method statement and Deviation schedule for the Hydrogen generation plant, in line with the requirements listed in the standards and specifications. This method statement must clearly demonstrate a complete understanding of, and capability to perform the civil scope of work Note: Any other relevant information needed to demonstrate a compliance to civil requirement can be submitted | 50
6.2 | The CV’s of the Lead Discipline Engineer or Technologist (or other CV’s of key personnel within the Civil Engineering field who are involved during the design, construction or commissioning phase of the project) will be evaluated to ensure a minimum of 5 years’ experience and professional registrations with the respective Governing bodies (such as ECSA or Equivalent) | 50

## Slide 15: Fire Protection (10%)
Ref | Criteria | Wt.
7.1 | The firefighting system (Protection System) meets the provisions of specified standards. Full achievement of the requirements specified in the enquiry, demonstrated strengths, no errors, weaknesses or omissions. Excellent response which demonstrates the ability to deliver the Fire Protection scope far in excess of minimum requirements. “The tenderer is required to provide a method statement detailing how they intend to comply with the fire protection sections of 240-RT&D-151 Specification for Renewable Hydrogen Facility. This method statement must include the fire protection high level design base, technical data sheets for proposed equipment, plant & instrumentation. Proof of the offered system compliance with the latest version of SANS 10139.” | 40
7.2 | Fire Detection System: The fire detection system meets the provisions of specified standards. Full achievement of the requirements specified in the enquiry, demonstrated strengths, no errors, weaknesses or omissions. | 30
7.3 | By virtue of the Department of Employment and Labour (DEOL) mandate to the South African Qualifications and Certification Committee (SAQCC), any person designing, installing, commissioning or maintaining Fire Detection System needs to be certified by SAQCC at the appropriate level. The Contractor or the nominated sub-contractor provides proof of paid-up valid registration with the SAQCC-fire. The proof is submitted as the following documents: Fire Detection System: Proof of certification with FDIA (Fire Detection Installers Association) or FSIB (Fire Support Interoperability Board). Person’s SAQCC registration card, with visible registration number and category registered for. Signed commitment of undertaking between the Contractor and the nominated sub-contractor if the registered person if associated with a sub-contractor. *Where the Contractor provides certificate(s) of the registered person(s), it is accompanied by the person(s) C.V. | 30

## Slide 16: Quality Assurance (5%)
Ref | Criteria | Wt.
8.1 | Procedures for installation and commissioning show compliance to requirements for Hazloc, Elec. Installation & Motors Testing, with indicated compliance to SANS 10142 (Elec. Installations) and SANS 10108 (Hazloc), as a minimum. | 40
8.2 | Quality Control Plan | 30
8.3 | Reference Check Sheets | 30

## Slide 17: Tips for Submission
‘20260417 Tender Returnable Technical Schedule’ is a guideline on what is required in the tender submission. Use the tables provided to double check that all requirement are submitted.
File names or document titles can include the section number used in the Evaluation Strategy and the Tender Returnable Technical Schedule
Submit all available information as the evaluation team cannot make assumption, use information in the media or past experience/project with the supplier.
Main sections in the costing schedule must remain the same. Provide a detailed breakdown under each section
Information provided in the submission will be contractual. Ensure you are able to deliver on what you have committed in the submission.

## Slide 18: Questions