## Price List and CPA
Contract |  | : | Supply and Delivery of RTD's and Thermocouples Scope of Work
Contract Type |  | : | 36 Months
Contract Location |  | : | Medupi Power Station-Lephalale, Limpopo Province
Document |  | : | Cost Estimate
Revision |  | : | Revision 2
Date |  | : | 2026-05-20
Item No. | Material | Material short description | Material full description | Quantity | Rate | Amount
1 | 574040 | DETECTOR RT:PT100;0-120 DEG C;60 MM;2;6 | DETECTOR, RESISTANCE TEMPERATURE: TYPE: PT100; TEMPERATURE RATING: 0-120 DEG C; RESISTANCE: 0.2 OHM 20 MILLIOHM/DEGREE; SHEATH LENGTH: 60 MM; WIRE: 2; SHEATH MATERIAL: SS GR 316; PROCESS CONNECTION: 1/2 IN BSPT COMPRESSION FITTING; HEAD: YES; TOLERANCE: 0.3 DEG C; SHEATH DIAMETER: 6 MM; NUMBER OF SENSORS: SINGLE; MANUF P/N: T1 RAA 1 SS 60; HEAD MATERIAL: DIE CAST ALLOY; FOR USE ON SSC HYDRAULIC OIL TANK TEMPERATURE MEASUREMENT | 10
2 | 574050 | DETECTOR RT:PT100;200 DEG C;80 MM;3;80;6 | DETECTOR, RESISTANCE TEMPERATURE: TYPE: PT100; TEMPERATURE RATING: 200 DEG C; RESISTANCE: 100 OHM AT 0 DEG C; SHEATH LENGTH: 80 MM; WIRE: 3; SHEATH SIZE: 80 MM; SHEATH MATERIAL: SS GR 316; PROCESS CONNECTION: 1/2 IN-NPT SS COMPRESSION FITTING; HEAD: YES; SHEATH DIAMETER: 6 MM; NUMBER OF SENSORS: SINGLE; MANUF P/N: G RX96-.3-80-FM-100-C-4F4S; HEAD MATERIAL: DIE CAST ALLOY; FOR USE ON SSC WATER TEMP MEASUREMENT | 10
3 | 645209 | DETECTOR RT:2 X PT100;3 | DETECTOR, RESISTANCE TEMPERATURE: TYPE: 2 X PT100; WIRE: 3; SUPPL P/N: TSP111-Y0W1M2U4S1D6P5S1B2T1 | 6
4 | 646022 | THERMOCOUPLE | THERMOCOUPLE: SUPPL P/N: 206.00996310 | 12 |  |  | Latest from SAP data taken
5 | 646023 | THERMOCOUPLE | THERMOCOUPLE: SUPPL P/N: 206.00997110 | 12 |  |  | Latest from SAP data taken
6 | 646396 | SENSOR TEMP:0-300 DEG C;INSERTION;IP20 | SENSOR, TEMPERATURE: MAXIMUM OPERATING TEMP: 0-300 DEG C; STYLE DESIGNATOR: INSERTION; INCLOSURE TYPE: IP20; OUTPUT SIGNAL: 4-20 MA; SUPPL P/N: PT100; REFERENCE NO: SENSY TEMP IS; PROBE DIAMETER 3MM; RTD LENGTH 315MM; 3 WIRE | 10
7 | 663453 | SENSOR TEMP:-200 TO 600 DEG C;MEASURING | SENSOR, TEMPERATURE: MAXIMUM OPERATING TEMP: -200 TO 600 DEG C; STYLE DESIGNATOR: MEASURING; MANUF P/N: TLSR1-YBB1112; PT100 IMMERSION LENGTH 100MM; SHEATH LENGTH 140MM; SHEATH DIAMETER 6MM; PROCESS CONNECTION 1/2 INCH BSPP; COMPLETE WITH HEAD; NUMBER OF SENSORS SINGLE | 14
8 | 665658 | THERMOCOUPLE:K;6 MM;375 MM;0-600 DEG C;4 | THERMOCOUPLE: TYPE: K; SHEATH DIAMETER: 6 MM; DESIGN LENGTH: 375 MM; TEMPERATURE RANGE: 0-600 DEG C; SHEATH MATERIAL: SS 2.4816; PROCESS CONNECTION: M18 X 1.5 MM; JUNCTION: DUAL; HEAD: YES; WIRES: 4; SPECIFICATION: NICR-NI ACC TO DIN EN 60584; CLASS 1; ELECTRICAL CONNECTION: M24 X 1.5 MM; SUPPL P/N: 1135-11-273(1-2009-17-R0); INCONEL 600; PROBE LG: 375MM; INSERTION LG: 200MM; NECK LG: 150MM; HEAD WITH HINGED COVER BUZH | 12
9 | 674850 | DETECTOR RT:PT100;-200 TO 600 DEG C;375 | DETECTOR, RESISTANCE TEMPERATURE: TYPE: PT100; TEMPERATURE RATING: -200 TO 600 DEG C; RESISTANCE: 100 OHM AT 0 DEG C; SHEATH LENGTH: 375 MM; WIRE: 4; SHEATH MATERIAL: SS GR 316L; PROCESS CONNECTION: CERAMIC TERMINAL BLOCK; SHEATH DIAMETER: 3 MM; NUMBER OF SENSORS: SINGLE | 50
10 | 681660 | DETECTOR RT:PT100;-200 TO 600 DEG C;430 | DETECTOR, RESISTANCE TEMPERATURE: TYPE: PT100; TEMPERATURE RATING: -200 TO 600 DEG C; RESISTANCE: 100 OHM AT 0 DEG C; SHEATH LENGTH: 430 MM; WIRE: 4; SHEATH MATERIAL: METAL; SHEATH DIAMETER: 6 MM; SUPPL P/N: S10, D91046; RUEGER | 30 |  |  | Pro rata item '2' above
11 | 694039 | SENSOR TEMP:-40 TO 125 DEG C;IP65;BASE | SENSOR, TEMPERATURE: MAXIMUM OPERATING TEMP: -40 TO 125 DEG C; STYLE DESIGNATOR: THERMISTOR DUCT; INCLOSURE TYPE: IP65; MOUNT: BASE; SUPPL P/N: TDN-NTC-10K-200; PROBE LG 200MM; OUTPUT TYPE: 2 WIRE | 10 |  |  | Pro rata item 7
12 | 722491 | SENSOR TEMP:450 DEG C;4 WIRE PT100 | SENSOR, TEMPERATURE: MAXIMUM OPERATING TEMP: 450 DEG C; STYLE DESIGNATOR: 4 WIRE PT100; MOUNT: CONNECTION HEAD; OUTPUT SIGNAL: 4-20 MA; SPECIFICATION: IEC751 STANDARD; IP67 RATING; SUPPL P/N: 872-2723; -100 | 20
13 | DCF to be completed | Gas Air heater Flue gas temps Inlet & Outlets | SENSOR, TEMPERATURE: MAXIMUM OPERATING TEMP: -4 - 1000 DEG C; STYLE DESIGNATOR: 2X TC TYPE K; INCLOSURE TYPE: IP 66; MOUNT: SHEATH DIAMETER: 6 MM; DESIGN LENGTH: 2080MM X 125MM X 125MM; POTENTIAL: 11 TO 42 VDC; OUTPUT: 4-20MA HART; TEMPERATURE RANGE: -4 TO 1000 DEG C; CALIBRATION RANGE: 0 TO +800 DEG C; OUTPUT SIGNAL: 4-20 MA; SPECIFICATION: SHEATH MATERIAL: STAINLESS STEEL; THERMOWELL: 22MM PROTECTION TUBE; PROCESS CONNECTION: 1 INCH MALE THREAD FITTING; ENCLOSURE: IP66; REFERENCE SERIAL NR: 210004431059004; MANUF P/N: Y0H2B1A05B1Y0Z9T1K2T2B2H4/OPT | 20 |  |  | Pro rata item 21
14 | DCF to be completed | Gas Air heater Flue gas temps Inlet & Outlets | THERMOCOUPLE: TYPE: 2X TC TYPE K; SHEATH DIAMETER: 6 MM; DESIGN LENGTH: 2235MM X 125MM X 125MM; POTENTIAL: 11 TO 42 VDC; OUTPUT: 4-20MA HART; TEMPERATURE RANGE: -4 TO 1000 DEG C; CALIBRATION RANGE: 0 TO +800 DEG C; SHEATH MATERIAL: STAINLESS STEEL; THERMOWELL: 22MM PROTECTION TUBE; PROCESS CONNECTION: 1 INCH MALE THREAD FITTING; ENCLOSURE: IP66; OEM P/N: Y0H2B1A05B1Y0Z9T1K2T2B2H4/OPT; REFERENCE SERIAL NR: 210004441099017 | 20
15 | DCF to be completed | Resistance temperature detector 250mm 3-wire Simplex (Head type R96) | DETECTOR, RESISTANCE TEMPERATURE: TYPE: MINERAL INSULATED; TEMPERATURE RATING: -200...+600 DEG C; RESISTANCE: @0 DEGC = 100 OHM; SHEATH LENGTH: 250 MM; WIRE: 3 WIRE SIMPLEX ASSEMBLY; SHEATH DIAMETER: 6 MM; SHEATH MATERIAL: STAINLESS STEEL 316SS; PROCESS CONNECTION: 1/2 INCH BSP; HEAD TYPE: R96 DIE CAST ALLOY; SIGNAL OUTPUT: OHMS; ENCLOSURE RATING: IP66/67; MOUNT: SUPPLY WITH STAINLESS STEEL ADJUSTABLE COMPRESSION FITTING 1/2 INCH BSP MALE THREAD 4F4S-1/2" BSP; APPLICATION: ELECTRICAL MOTOR PT100 RTD'S; NUMBER OF SENSORS: 1XPT100 / 3 WIRE; OEM P/N: LR96.3-250FM(100)C-4F4SBSP | 20
16 | DCF to be completed | Resistance temperature detector 250mm 4-wire Duplex (Head type R96) | DETECTOR, RESISTANCE TEMPERATURE: TYPE: MINERAL INSULATED; TEMPERATURE RATING: -200...+600 DEG C; RESISTANCE: @0 DEGC = 100 OHM; SHEATH LENGTH: 250 MM; WIRE: 4 WIRE DUPLEX ASSEMBLY; SHEATH DIAMETER: 6 MM; SHEATH MATERIAL: STAINLESS STEEL 316SS; PROCESS CONNECTION: 1/2 INCH BSP; HEAD TYPE: R96 DIE CAST ALLOY; SIGNAL OUTPUT: OHMS; ENCLOSURE RATING: IP66/67; MOUNT: SUPPLY WITH STAINLESS STEEL ADJUSTABLE COMPRESSION FITTING 1/2 INCH BSP MALE THREAD 4F4S-1/2" BSP; APPLICATION: ELECTRICAL MOTOR PT100 RTD'S; NUMBER OF SENSORS: 2XPT100 / 8 WIRE; OEM P/N: LR96.8-250FM(100)C-4F4SBSP | 20
17 | DCF to be completed | Resistance temperature detector 250mm 3-wire Duplex (Head type R96) | DETECTOR, RESISTANCE TEMPERATURE: TYPE: MINERAL INSULATED; TEMPERATURE RATING: -200...+600 DEG C; RESISTANCE: @0 DEGC = 100 OHM; SHEATH LENGTH: 250 MM; WIRE: 3 WIRE DUPLEX ASSEMBLY; SHEATH DIAMETER: 6 MM; SHEATH MATERIAL: STAINLESS STEEL 316SS; PROCESS CONNECTION: 1/2 INCH BSP; HEAD TYPE: R96 DIE CAST ALLOY; SIGNAL OUTPUT: OHMS; ENCLOSURE RATING: IP66/67; MOUNT: SUPPLY WITH STAINLESS STEEL ADJUSTABLE COMPRESSION FITTING 1/2 INCH BSP MALE THREAD 4F4S-1/2" BSP; APPLICATION: ELECTRICAL MOTOR PT100 RTD'S; NUMBER OF SENSORS: 2XPT100 / 6 WIRE; OEM P/N: LR96.6-250FM(100)C-4F4SBSP | 20
18 | DCF to be completed | Resistance temperature detector 200mm 3-wire Duplex with 4 metres tail | DETECTOR, RESISTANCE TEMPERATURE: TYPE: MINERAL INSULATED; TEMPERATURE RATING: -200...+600 DEG C; RESISTANCE: @0 DEGC = 100 OHM; SHEATH LENGTH: 200 MM WITH A TAIL LENGTH OF 4 METRES; WIRE: 3 WIRE DUPLEX ASSEMBLY; SHEATH DIAMETER: 6 MM; SHEATH MATERIAL: STAINLESS STEEL 316SS; PROCESS CONNECTION: 1/2 INCH BSP; HEAD TYPE: R26 TAIL WITH SPRAGUE TUBING; SIGNAL OUTPUT: OHMS; ENCLOSURE RATING: IP66/67; MOUNT: SUPPLY WITH STAINLESS STEEL ADJUSTABLE COMPRESSION FITTING 1/2 INCH BSP MALE THREAD 4F4S-1/2" BSP; APPLICATION: ELECTRICAL MOTOR PT100 RTD'S; NUMBER OF SENSORS: 2XPT100 / 6 WIRE; OEM P/N: LR26.6-200FM(100)C4000P-4F4SBSP | 20
19 | DCF to be completed | Resistance temperature detector 250mm 4-wire (Head type R96) | DETECTOR, RESISTANCE TEMPERATURE: TYPE: MINERAL INSULATED; TEMPERATURE RATING: -200...+600 DEG C; RESISTANCE: @0 DEGC = 100 OHM; SHEATH LENGTH: 250 MM; WIRE: 4 WIRE SIMPLEX ASSEMBLY; SHEATH DIAMETER: 6 MM; SHEATH MATERIAL: STAINLESS STEEL 316SS; PROCESS CONNECTION: 1/2 INCH BSP; HEAD TYPE: R96 DIE CAST ALLOY; SIGNAL OUTPUT: OHMS; ENCLOSURE RATING: IP66/67; MOUNT: SUPPLY WITH STAINLESS STEEL ADJUSTABLE COMPRESSION FITTING 1/2 INCH BSP MALE THREAD 4F4S-1/2" BSP; APPLICATION: FEEDWATER AND CONDENSATE SYSTEM N30 RTD'S; NUMBER OF SENSORS: 1XPT100 / 4 WIRE; OEM P/N: LR96.4-250FM(100)C-4F4SBSP | 20
20 | DCF to be completed | Thermocouple 200mm Tail 2,5 metres | THERMOCOUPLE: TYPE: MINERAL INSULATED; TEMPERATURE RATING: -200...+1100 DEG C; SHEATH LENGTH: 200 MM WITH A TAIL LENGTH OF 2,5 METRES;; WIRE: 4 WIRES / DUPLEX ASSEMBLY; SHEATH DIAMETER: 6 MM; SHEATH MATERIAL: 25/20 CHROMIUM/NICKEL STAINLESS STEEL TO BS 970 PART 4: 1970, GRADE 310S24; PROCESS CONNECTION: 1/2 INCH BSP; HEAD TYPE: T26 TAIL WITH SPRAGUE TUBING; SIGNAL OUTPUT: MILLI-VOLTS; ENCLOSURE RATING: IP66/67; MOUNT: SUPPLY WITH STAINLESS STEEL ADJUSTABLE COMPRESSION FITTING 1/2 INCH BSP MALE THREAD 4F4S-1/2" BSP; APPLICATION: FEEDWATER AND CONDENSATE PIPING SYSTEMS; NUMBER OF SENSORS: 4 WIRES / DUPLEX ASSEMBLY WITH TYPE 9 INSULATED HOT JUNCTION FROM THE SHEATH; OEM P/N: T26.4-200FMK9D2500P-4F4SBSP | 20
21 | DCF to be completed | Thermocouple 250mm Head type T96 | THERMOCOUPLE: TYPE: MINERAL INSULATED; TEMPERATURE RATING: -200...+1100 DEG C; SHEATH LENGTH: 250 MM; WIRE: 4 WIRES / DUPLEX ASSEMBLY; SHEATH DIAMETER: 6 MM; SHEATH MATERIAL: 25/20 CHROMIUM/NICKEL STAINLESS STEEL TO BS 970 PART 4: 1970, GRADE 310S24; PROCESS CONNECTION: 1/2 INCH BSP; HEAD TYPE: T96 DIE CAST ALLOY; SIGNAL OUTPUT: MILLI-VOLTS; ENCLOSURE RATING: IP66/67; MOUNT: SUPPLY WITH STAINLESS STEEL ADJUSTABLE COMPRESSION FITTING 1/2 INCH BSP MALE THREAD 4F4S-1/2" BSP; APPLICATION: FEEDWATER AND CONDENSATE PIPING SYSTEMS; NUMBER OF SENSORS: 4 WIRES / DUPLEX ASSEMBLY WITH TYPE 9 INSULATED HOT JUNCTION FROM THE SHEATH; OEM P/N: T96.4-250FMK9D-4F4SBSP | 20
22 | DCF to be completed | Resistance temperature detector 200mm 3-wire Duplex with 2,5 metres tail | DETECTOR, RESISTANCE TEMPERATURE: TYPE: MINERAL INSULATED; TEMPERATURE RATING: -200...+600 DEG C; RESISTANCE: @0 DEGC = 100 OHM; SHEATH LENGTH: 200 MM WITH A TAIL LENGTH OF 2,5 METRES; WIRE: 3 WIRE DUPLEX ASSEMBLY; SHEATH DIAMETER: 6 MM; SHEATH MATERIAL: STAINLESS STEEL 316SS; PROCESS CONNECTION: 1/2 INCH BSP; HEAD TYPE: R26 TAIL WITH SPRAGUE TUBING; SIGNAL OUTPUT: OHMS; ENCLOSURE RATING: IP66/67; MOUNT: SUPPLY WITH STAINLESS STEEL ADJUSTABLE COMPRESSION FITTING 1/2 INCH BSP MALE THREAD 4F4S-1/2" BSP; APPLICATION: ELECTRICAL MOTOR PT100 RTD'S; NUMBER OF SENSORS: 2XPT100 / 6 WIRE; OEM P/N: LR26.6-200FM(100)C2500P-4F4SBSP | 20
TOTAL (EXCL. VAT)
The proportions used to calculate the Price Adjustment Factor are:
Proportion Linked to index for Index prepared by
65% [Electrical Engineering] SEIFSA: TABLE G-1
20% [Transport] SEIFSA: Table L-1 (B)
15% non-adjustable
100%